## Sheet1
Short-Circuit - Fault Locations with Feeders
Project | IEEE 118bus_modified
Study Case | ShortCircuit
Method | complete
3-Phase Short-Circuit | / Max. Short-Circuit Currents
Short-Circuit Duration | Break Time Fault Clearing Time (Ith)
0.10 s 1.00 s
Fault Impedance | Resistance, Rf Reactance, Xf
0.00 Ohm 0.00 Ohm
Operation Scenario | ShortCircuit
0 | Terminal | Grid | Connected Element (Branch) | Nominal Voltage (kV) | Fault Voltage (kV) | Fault Voltage Angle (deg) | c-Factor | Sk" (MVA) | Ik" (kA) | Ik" Angle (deg) | Ik (kA) | Ik Angle (deg) | ip (kA) | Ib (kA) | ib (kA) | Ith (kA)
1 | B20 | IEEE 118 Bus Test Case | Connected Element (Branch) | 230 | 0 | 0 | -1 | 755.5455 | 1.8966 | -46.9981 | 1.8625 | -46.86 | 4.1673 | 1.8653 | 2.6439 | 1.9126
2 | B20 | IEEE 118 Bus Test Case | Line 19-20 | 230 | 0 | 0 | -1 | 522.0202 | 1.3104 | 131.53 | 1.2883 | 131.6613 | 2.8792 | 1.8653 | 2.6439 | 1.9126
3 | B20 | IEEE 118 Bus Test Case | Line 20-21 | 230 | 0 | 0 | -1 | 234.0819 | 0.5876 | 136.2856 | 0.57564 | 136.4508 | 1.2911 | 1.8653 | 2.6439 | 1.9126
4 | B20 | IEEE 118 Bus Test Case | Load 20 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8653 | 2.6439 | 1.9126
5 | B96 | IEEE 118 Bus Test Case | Load 20 | 230 | 0 | 0 | -1 | 2391.9859 | 6.0044 | -40.64 | 5.7014 | -40.5826 | 13.0746 | 5.7263 | 8.1217 | 6.0529
6 | B96 | IEEE 118 Bus Test Case | Line 95-96 | 230 | 0 | 0 | -1 | 418.5743 | 1.0507 | 146.3164 | 0.98327 | 146.7297 | 2.2879 | 5.7263 | 8.1217 | 6.0529
7 | B96 | IEEE 118 Bus Test Case | Line 80-96 | 230 | 0 | 0 | -1 | 435.732 | 1.0938 | 131.5436 | 1.0462 | 131.4532 | 2.3817 | 5.7263 | 8.1217 | 6.0529
8 | B96 | IEEE 118 Bus Test Case | Line 82-96 | 230 | 0 | 0 | -1 | 641.5803 | 1.6105 | 140.0849 | 1.5473 | 140.0729 | 3.5069 | 5.7263 | 8.1217 | 6.0529
9 | B96 | IEEE 118 Bus Test Case | Line 96-97 | 230 | 0 | 0 | -1 | 434.1105 | 1.0897 | 131.1971 | 1.0423 | 131.1067 | 2.3729 | 5.7263 | 8.1217 | 6.0529
10 | B96 | IEEE 118 Bus Test Case | Line 94-96 | 230 | 0 | 0 | -1 | 477.6209 | 1.1989 | 146.8292 | 1.122 | 147.2425 | 2.6107 | 5.7263 | 8.1217 | 6.0529
11 | B96 | IEEE 118 Bus Test Case | Load 96 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7263 | 8.1217 | 6.0529
12 | B85 | IEEE 118 Bus Test Case | Load 96 | 230 | 0 | 0 | -1 | 1530.272 | 3.8413 | -38.7256 | 3.6579 | -38.6898 | 8.6933 | 3.673 | 5.2828 | 3.8788
13 | B85 | IEEE 118 Bus Test Case | Gen 85 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.673 | 5.2828 | 3.8788
14 | B85 | IEEE 118 Bus Test Case | Line 85-88 | 230 | 0 | 0 | -1 | 414.6448 | 1.0408 | 143.5082 | 0.9925 | 143.7216 | 2.3556 | 3.673 | 5.2828 | 3.8788
15 | B85 | IEEE 118 Bus Test Case | Line 83-85 | 230 | 0 | 0 | -1 | 290.0406 | 0.72807 | 134.6364 | 0.71328 | 134.4773 | 1.6477 | 3.673 | 5.2828 | 3.8788
16 | B85 | IEEE 118 Bus Test Case | Line 85-89 | 230 | 0 | 0 | -1 | 422.1747 | 1.0598 | 141.4332 | 1.0105 | 141.6466 | 2.3983 | 3.673 | 5.2828 | 3.8788
17 | B85 | IEEE 118 Bus Test Case | Line 84-85 | 230 | 0 | 0 | -1 | 205.1112 | 0.51487 | 143.5143 | 0.50442 | 143.3552 | 1.1652 | 3.673 | 5.2828 | 3.8788
18 | B85 | IEEE 118 Bus Test Case | Line 85-86 | 230 | 0 | 0 | -1 | 200.8851 | 0.50427 | 143.6081 | 0.4439 | 143.7852 | 1.1412 | 3.673 | 5.2828 | 3.8788
19 | B85 | IEEE 118 Bus Test Case | Load 85 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.673 | 5.2828 | 3.8788
20 | B74 | IEEE 118 Bus Test Case | Load 85 | 230 | 0 | 0 | -1 | 1257.6425 | 3.157 | -44.4728 | 3.0978 | -44.4204 | 6.5423 | 3.1026 | 4.3915 | 3.1775
21 | B74 | IEEE 118 Bus Test Case | Gen 74 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1026 | 4.3915 | 3.1775
22 | B74 | IEEE 118 Bus Test Case | Shunt 74 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1026 | 4.3915 | 3.1775
23 | B74 | IEEE 118 Bus Test Case | Load 74 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1026 | 4.3915 | 3.1775
24 | B74 | IEEE 118 Bus Test Case | Line 70-74 | 230 | 0 | 0 | -1 | 368.3653 | 0.92468 | 135.6635 | 0.90813 | 135.7093 | 1.9162 | 3.1026 | 4.3915 | 3.1775
25 | B74 | IEEE 118 Bus Test Case | Line 74-75 | 230 | 0 | 0 | -1 | 889.2787 | 2.2323 | 135.4708 | 2.1896 | 135.5258 | 4.626 | 3.1026 | 4.3915 | 3.1775
26 | B9 | IEEE 118 Bus Test Case | Line 74-75 | 500 | 0 | 0 | -1 | 2605.0132 | 3.008 | -53.0352 | 2.695 | -52.8585 | 7.7498 | 2.7207 | 4.529 | 3.0837
27 | B9 | IEEE 118 Bus Test Case | Line 9-10 | 500 | 0 | 0 | -1 | 1506.1343 | 1.7391 | 125.6199 | 1.4895 | 125.3492 | 4.4807 | 2.7207 | 4.529 | 3.0837
28 | B9 | IEEE 118 Bus Test Case | Line 8-9 | 500 | 0 | 0 | -1 | 1099.862 | 1.27 | 128.8066 | 1.2071 | 129.3532 | 3.2721 | 2.7207 | 4.529 | 3.0837
29 | B84 | IEEE 118 Bus Test Case | Line 8-9 | 230 | 0 | 0 | -1 | 998.8491 | 2.5073 | -33.0746 | 2.4405 | -33.2319 | 4.9923 | 2.446 | 3.4597 | 2.5213
30 | B84 | IEEE 118 Bus Test Case | Load 84 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.446 | 3.4597 | 2.5213
31 | B84 | IEEE 118 Bus Test Case | Line 83-84 | 230 | 0 | 0 | -1 | 366.2983 | 0.91949 | 143.7522 | 0.90254 | 143.5891 | 1.8308 | 2.446 | 3.4597 | 2.5213
32 | B84 | IEEE 118 Bus Test Case | Line 84-85 | 230 | 0 | 0 | -1 | 633.437 | 1.5901 | 148.7598 | 1.5402 | 148.6304 | 3.1659 | 2.446 | 3.4597 | 2.5213
33 | B108 | IEEE 118 Bus Test Case | Line 84-85 | 230 | 0 | 0 | -1 | 971.9438 | 2.4398 | -34.044 | 2.2499 | -34.2989 | 5.1053 | 2.2655 | 3.2068 | 2.4563
34 | B108 | IEEE 118 Bus Test Case | Line 108-109 | 230 | 0 | 0 | -1 | 398.1651 | 0.99948 | 148.0674 | 0.8908 | 147.6468 | 2.0914 | 2.2655 | 3.2068 | 2.4563
35 | B108 | IEEE 118 Bus Test Case | Line 105-108 | 230 | 0 | 0 | -1 | 574.2364 | 1.4415 | 144.4921 | 1.36 | 144.4268 | 3.0163 | 2.2655 | 3.2068 | 2.4563
36 | B108 | IEEE 118 Bus Test Case | Load 108 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2655 | 3.2068 | 2.4563
37 | B98 | IEEE 118 Bus Test Case | Load 108 | 230 | 0 | 0 | -1 | 1268.2026 | 3.1835 | -43.0547 | 3.0748 | -42.947 | 7.0535 | 3.0838 | 4.3761 | 3.2114
38 | B98 | IEEE 118 Bus Test Case | Line 98-100 | 230 | 0 | 0 | -1 | 471.3504 | 1.1832 | 142.5121 | 1.131 | 142.9234 | 2.6216 | 3.0838 | 4.3761 | 3.2114
39 | B98 | IEEE 118 Bus Test Case | Load 98 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0838 | 4.3761 | 3.2114
40 | B98 | IEEE 118 Bus Test Case | Line 80-98 | 230 | 0 | 0 | -1 | 800.3824 | 2.0091 | 133.6703 | 1.9532 | 133.6577 | 4.4516 | 3.0838 | 4.3761 | 3.2114
41 | B10 | IEEE 118 Bus Test Case | Line 80-98 | 500 | 0 | 0 | -1 | 3631.5732 | 4.1934 | -55.0336 | 3.3854 | -54.8651 | 11.2601 | 3.4517 | 7.4079 | 4.3854
42 | B10 | IEEE 118 Bus Test Case | Line 9-10 | 500 | 0 | 0 | -1 | 823.2105 | 0.95056 | 128.009 | 0.91501 | 128.4396 | 2.5525 | 3.4517 | 7.4079 | 4.3854
43 | B10 | IEEE 118 Bus Test Case | Tx 10-119 | 500 | 0 | 0 | -1 | 2809.8629 | 3.2446 | 124.0754 | 2.4725 | 123.9125 | 8.7123 | 3.4517 | 7.4079 | 4.3854
44 | B80 | IEEE 118 Bus Test Case | Tx 10-119 | 230 | 0 | 0 | -1 | 6079.8779 | 15.2618 | -49.5318 | 13.1588 | -48.6827 | 38.9248 | 13.3314 | 27.0881 | 15.6066
45 | B80 | IEEE 118 Bus Test Case | Line 80-96 | 230 | 0 | 0 | -1 | 210.6697 | 0.52883 | 141.6002 | 0.49402 | 142.3684 | 1.3488 | 13.3314 | 27.0881 | 15.6066
46 | B80 | IEEE 118 Bus Test Case | Line 80-98 | 230 | 0 | 0 | -1 | 250.1822 | 0.62801 | 142.3218 | 0.57317 | 143.5226 | 1.6017 | 13.3314 | 27.0881 | 15.6066
47 | B80 | IEEE 118 Bus Test Case | Tx 81-80 | 230 | 0 | 0 | -1 | 1232.8459 | 3.0947 | 121.5092 | 2.9435 | 121.5925 | 7.893 | 13.3314 | 27.0881 | 15.6066
48 | B80 | IEEE 118 Bus Test Case | Load 80 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 13.3314 | 27.0881 | 15.6066
49 | B80 | IEEE 118 Bus Test Case | Line 80-99 | 230 | 0 | 0 | -1 | 248.9891 | 0.62502 | 144.6667 | 0.57044 | 145.8674 | 1.5941 | 13.3314 | 27.0881 | 15.6066
50 | B80 | IEEE 118 Bus Test Case | Line 77-80 C1 | 230 | 0 | 0 | -1 | 462.5899 | 1.1612 | 138.8382 | 1.0992 | 139.0017 | 2.9616 | 13.3314 | 27.0881 | 15.6066
51 | B80 | IEEE 118 Bus Test Case | Line 80-97 | 230 | 0 | 0 | -1 | 209.8857 | 0.52686 | 141.2538 | 0.49218 | 142.0219 | 1.3437 | 13.3314 | 27.0881 | 15.6066
52 | B80 | IEEE 118 Bus Test Case | Line 79-80 | 230 | 0 | 0 | -1 | 211.885 | 0.53188 | 131.7954 | 0.50348 | 131.9589 | 1.3565 | 13.3314 | 27.0881 | 15.6066
53 | B80 | IEEE 118 Bus Test Case | Line 77-80 C2 | 230 | 0 | 0 | -1 | 218.0327 | 0.54731 | 135.1641 | 0.51809 | 135.3276 | 1.3959 | 13.3314 | 27.0881 | 15.6066
54 | B80 | IEEE 118 Bus Test Case | Tx 80-132 | 230 | 0 | 0 | -1 | 3077.4988 | 7.7252 | 128.7826 | 6.0688 | 129.9743 | 19.7029 | 13.3314 | 27.0881 | 15.6066
55 | B95 | IEEE 118 Bus Test Case | Tx 80-132 | 230 | 0 | 0 | -1 | 1740.9683 | 4.3702 | -38.1706 | 4.1794 | -38.1682 | 9.2265 | 4.1951 | 5.9378 | 4.401
56 | B95 | IEEE 118 Bus Test Case | Line 94-95 | 230 | 0 | 0 | -1 | 961.1652 | 2.4127 | 144.774 | 2.2886 | 144.9158 | 5.0938 | 4.1951 | 5.9378 | 4.401
57 | B95 | IEEE 118 Bus Test Case | Line 95-96 | 230 | 0 | 0 | -1 | 782.6311 | 1.9646 | 138.2124 | 1.8981 | 138.1125 | 4.1477 | 4.1951 | 5.9378 | 4.401
58 | B95 | IEEE 118 Bus Test Case | Load 95 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1951 | 5.9378 | 4.401
59 | B79 | IEEE 118 Bus Test Case | Load 95 | 230 | 0 | 0 | -1 | 2323.1247 | 5.8316 | -45.5388 | 5.5582 | -45.3688 | 12.8955 | 5.5807 | 7.929 | 5.8822
60 | B79 | IEEE 118 Bus Test Case | Line 79-80 | 230 | 0 | 0 | -1 | 994.0979 | 2.4954 | 133.7794 | 2.3641 | 133.9869 | 5.5182 | 5.5807 | 7.929 | 5.8822
61 | B79 | IEEE 118 Bus Test Case | Load 79 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5807 | 7.929 | 5.8822
62 | B79 | IEEE 118 Bus Test Case | Line 78-79 | 230 | 0 | 0 | -1 | 1329.1498 | 3.3365 | 134.9712 | 3.1944 | 135.108 | 7.378 | 5.5807 | 7.929 | 5.8822
63 | B79 | IEEE 118 Bus Test Case | Shunt 79 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5807 | 7.929 | 5.8822
64 | B78 | IEEE 118 Bus Test Case | Shunt 79 | 230 | 0 | 0 | -1 | 2885.7517 | 7.2439 | -43.9426 | 6.8489 | -43.8191 | 15.7309 | 6.8813 | 9.7629 | 7.3016
65 | B78 | IEEE 118 Bus Test Case | Load 78 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8813 | 9.7629 | 7.3016
66 | B78 | IEEE 118 Bus Test Case | Line 78-79 | 230 | 0 | 0 | -1 | 677.5116 | 1.7007 | 132.6078 | 1.5923 | 132.7703 | 3.6933 | 6.8813 | 9.7629 | 7.3016
67 | B78 | IEEE 118 Bus Test Case | Line 77-78 | 230 | 0 | 0 | -1 | 2209.8437 | 5.5472 | 137.1144 | 5.2603 | 137.2127 | 12.0464 | 6.8813 | 9.7629 | 7.3016
68 | B103 | IEEE 118 Bus Test Case | Line 77-78 | 230 | 0 | 0 | -1 | 2385.695 | 5.9886 | -39.7412 | 4.9743 | -38.8347 | 14.1353 | 5.0576 | 8.8573 | 6.0627
69 | B103 | IEEE 118 Bus Test Case | Line 103-104 | 230 | 0 | 0 | -1 | 159.4957 | 0.40037 | 140.6585 | 0.35755 | 140.7728 | 0.94501 | 5.0576 | 8.8573 | 6.0627
70 | B103 | IEEE 118 Bus Test Case | Line 103-105 | 230 | 0 | 0 | -1 | 154.4423 | 0.38768 | 143.215 | 0.34387 | 143.2379 | 0.91507 | 5.0576 | 8.8573 | 6.0627
71 | B103 | IEEE 118 Bus Test Case | Line 100-103 | 230 | 0 | 0 | -1 | 1109.312 | 2.7846 | 143.4778 | 2.5257 | 143.811 | 6.5727 | 5.0576 | 8.8573 | 6.0627
72 | B103 | IEEE 118 Bus Test Case | Load 103 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0576 | 8.8573 | 6.0627
73 | B103 | IEEE 118 Bus Test Case | Line 103-110 | 230 | 0 | 0 | -1 | 204.3394 | 0.51294 | 143.9697 | 0.43338 | 143.9184 | 1.2107 | 5.0576 | 8.8573 | 6.0627
74 | B103 | IEEE 118 Bus Test Case | Tx 103-136 | 230 | 0 | 0 | -1 | 765.1842 | 1.9208 | 133.9116 | 1.3254 | 134.7805 | 4.5337 | 5.0576 | 8.8573 | 6.0627
75 | B89 | IEEE 118 Bus Test Case | Tx 103-136 | 230 | 0 | 0 | -1 | 3693.2551 | 9.2709 | -40.9227 | 8.0122 | -40.3139 | 24.1014 | 8.1156 | 20.4569 | 9.53
76 | B89 | IEEE 118 Bus Test Case | Line 85-89 | 230 | 0 | 0 | -1 | 194.4066 | 0.488 | 135.2886 | 0.46612 | 135.002 | 1.2687 | 8.1156 | 20.4569 | 9.53
77 | B89 | IEEE 118 Bus Test Case | Line 89-90 C2 | 230 | 0 | 0 | -1 | 59.8357 | 0.1502 | 142.161 | 0.14203 | 141.9428 | 0.39047 | 8.1156 | 20.4569 | 9.53
78 | B89 | IEEE 118 Bus Test Case | Line 89-90 C1 | 230 | 0 | 0 | -1 | 31.4516 | 0.07895 | 144.1394 | 0.074655 | 143.9212 | 0.20525 | 8.1156 | 20.4569 | 9.53
79 | B89 | IEEE 118 Bus Test Case | Line 89-92 C1 | 230 | 0 | 0 | -1 | 521.3034 | 1.3086 | 137.5053 | 1.2374 | 137.2871 | 3.4019 | 8.1156 | 20.4569 | 9.53
80 | B89 | IEEE 118 Bus Test Case | Line 88-89 | 230 | 0 | 0 | -1 | 190.9391 | 0.4793 | 137.3636 | 0.45781 | 137.077 | 1.246 | 8.1156 | 20.4569 | 9.53
81 | B89 | IEEE 118 Bus Test Case | Line 89-92 C2 | 230 | 0 | 0 | -1 | 164.6719 | 0.41336 | 140.3731 | 0.39087 | 140.155 | 1.0746 | 8.1156 | 20.4569 | 9.53
82 | B89 | IEEE 118 Bus Test Case | Tx 89-134 | 230 | 0 | 0 | -1 | 2531.7105 | 6.3551 | 139.601 | 5.2477 | 140.7387 | 16.5214 | 8.1156 | 20.4569 | 9.53
83 | B106 | IEEE 118 Bus Test Case | Tx 89-134 | 230 | 0 | 0 | -1 | 1043.176 | 2.6186 | -35.9856 | 2.4485 | -35.8765 | 5.6383 | 2.4625 | 3.4917 | 2.6387
84 | B106 | IEEE 118 Bus Test Case | Load 106 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4625 | 3.4917 | 2.6387
85 | B106 | IEEE 118 Bus Test Case | Line 106-107 | 230 | 0 | 0 | -1 | 89.2023 | 0.22392 | 146.0248 | 0.20818 | 146.1182 | 0.48214 | 2.4625 | 3.4917 | 2.6387
86 | B106 | IEEE 118 Bus Test Case | Line 100-106 | 230 | 0 | 0 | -1 | 348.1928 | 0.87404 | 143.5269 | 0.8266 | 143.675 | 1.882 | 2.4625 | 3.4917 | 2.6387
87 | B106 | IEEE 118 Bus Test Case | Line 105-106 | 230 | 0 | 0 | -1 | 605.8486 | 1.5208 | 143.9987 | 1.4139 | 144.092 | 3.2746 | 2.4625 | 3.4917 | 2.6387
88 | B23 | IEEE 118 Bus Test Case | Line 105-106 | 230 | 0 | 0 | -1 | 1773.1439 | 4.451 | -45.2297 | 4.1772 | -45.2095 | 10.2048 | 4.1997 | 6.0537 | 4.4975
89 | B23 | IEEE 118 Bus Test Case | Line 23-25 | 230 | 0 | 0 | -1 | 924.1825 | 2.3199 | 136.8231 | 2.1346 | 136.9046 | 5.3189 | 4.1997 | 6.0537 | 4.4975
90 | B23 | IEEE 118 Bus Test Case | Load 23 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1997 | 6.0537 | 4.4975
91 | B23 | IEEE 118 Bus Test Case | Line 23-24 | 230 | 0 | 0 | -1 | 286.0936 | 0.71816 | 127.6222 | 0.71145 | 127.6321 | 1.6465 | 4.1997 | 6.0537 | 4.4975
92 | B23 | IEEE 118 Bus Test Case | Line 22-23 | 230 | 0 | 0 | -1 | 153.487 | 0.38529 | 126.5991 | 0.37144 | 126.6295 | 0.88335 | 4.1997 | 6.0537 | 4.4975
93 | B23 | IEEE 118 Bus Test Case | Line 23-32 | 230 | 0 | 0 | -1 | 414.4692 | 1.0404 | 138.1327 | 0.9725 | 138.4833 | 2.3854 | 4.1997 | 6.0537 | 4.4975
94 | B13 | IEEE 118 Bus Test Case | Line 23-32 | 230 | 0 | 0 | -1 | 1038.2957 | 2.6063 | -44.0565 | 2.5107 | -43.9308 | 5.5713 | 2.5186 | 3.5662 | 2.6257
95 | B13 | IEEE 118 Bus Test Case | Line 13-15 | 230 | 0 | 0 | -1 | 277.8781 | 0.69753 | 134.7112 | 0.68039 | 134.8033 | 1.491 | 2.5186 | 3.5662 | 2.6257
96 | B13 | IEEE 118 Bus Test Case | Line 11-13 | 230 | 0 | 0 | -1 | 760.5054 | 1.909 | 136.3938 | 1.8306 | 136.5397 | 4.0807 | 2.5186 | 3.5662 | 2.6257
97 | B13 | IEEE 118 Bus Test Case | Load 13 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5186 | 3.5662 | 2.6257
98 | B117 | IEEE 118 Bus Test Case | Load 13 | 230 | 0 | 0 | -1 | 539.3859 | 1.354 | -45.6609 | 1.3189 | -45.4929 | 2.9745 | 1.3218 | 1.8756 | 1.3654
99 | B117 | IEEE 118 Bus Test Case | Line 12-117 | 230 | 0 | 0 | -1 | 539.3859 | 1.354 | 134.3391 | 1.3189 | 134.5071 | 2.9745 | 1.3218 | 1.8756 | 1.3654
100 | B117 | IEEE 118 Bus Test Case | Load 117 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3218 | 1.8756 | 1.3654
101 | B47 | IEEE 118 Bus Test Case | Load 117 | 230 | 0 | 0 | -1 | 1879.0886 | 4.7169 | -47.4437 | 4.413 | -47.0818 | 10.0221 | 4.4379 | 6.297 | 4.7511
102 | B47 | IEEE 118 Bus Test Case | Line 46-47 | 230 | 0 | 0 | -1 | 415.6961 | 1.0435 | 129.8959 | 0.93639 | 130.3443 | 2.2171 | 4.4379 | 6.297 | 4.7511
103 | B47 | IEEE 118 Bus Test Case | Line 47-49 | 230 | 0 | 0 | -1 | 1135.0048 | 2.8491 | 132.4513 | 2.6718 | 132.7968 | 6.0535 | 4.4379 | 6.297 | 4.7511
104 | B47 | IEEE 118 Bus Test Case | Line 47-69 | 230 | 0 | 0 | -1 | 329.5317 | 0.8272 | 136.2756 | 0.80715 | 136.3074 | 1.7576 | 4.4379 | 6.297 | 4.7511
105 | B47 | IEEE 118 Bus Test Case | Load 47 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4379 | 6.297 | 4.7511
106 | B111 | IEEE 118 Bus Test Case | Load 47 | 230 | 0 | 0 | -1 | 1120.1858 | 2.8119 | -39.5877 | 2.1951 | -38.6112 | 6.9787 | 2.2457 | 4.6201 | 2.6214
107 | B111 | IEEE 118 Bus Test Case | Line 110-111 | 230 | 0 | 0 | -1 | 445.4213 | 1.1181 | 143.2527 | 1.0775 | 143.1616 | 2.775 | 2.2457 | 4.6201 | 2.6214
108 | B111 | IEEE 118 Bus Test Case | Tx 111-137 | 230 | 0 | 0 | -1 | 675.6723 | 1.6961 | 138.5403 | 1.1186 | 139.6813 | 4.2094 | 2.2457 | 4.6201 | 2.6214
109 | B112 | IEEE 118 Bus Test Case | Tx 111-137 | 230 | 0 | 0 | -1 | 634.1726 | 1.5919 | -32.647 | 1.4687 | -33.0876 | 3.2974 | 1.4788 | 2.0928 | 1.6023
110 | B112 | IEEE 118 Bus Test Case | Gen 112 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4788 | 2.0928 | 1.6023
111 | B112 | IEEE 118 Bus Test Case | Line 110-112 | 230 | 0 | 0 | -1 | 634.1726 | 1.5919 | 147.353 | 1.4687 | 146.9124 | 3.2974 | 1.4788 | 2.0928 | 1.6023
112 | B112 | IEEE 118 Bus Test Case | Load 112 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4788 | 2.0928 | 1.6023
113 | B76 | IEEE 118 Bus Test Case | Load 112 | 230 | 0 | 0 | -1 | 1074.6824 | 2.6977 | -43.9181 | 2.6532 | -43.8436 | 5.528 | 2.6568 | 3.7584 | 2.7145
114 | B76 | IEEE 118 Bus Test Case | Gen 76 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6568 | 3.7584 | 2.7145
115 | B76 | IEEE 118 Bus Test Case | Line 76-77 | 230 | 0 | 0 | -1 | 526.8717 | 1.3226 | 137.7783 | 1.2996 | 137.8822 | 2.7101 | 2.6568 | 3.7584 | 2.7145
116 | B76 | IEEE 118 Bus Test Case | Load 76 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6568 | 3.7584 | 2.7145
117 | B76 | IEEE 118 Bus Test Case | Line 76-118 | 230 | 0 | 0 | -1 | 548.2635 | 1.3763 | 134.4517 | 1.3547 | 134.5008 | 2.8202 | 2.6568 | 3.7584 | 2.7145
118 | B113 | IEEE 118 Bus Test Case | Line 76-118 | 230 | 0 | 0 | -1 | 1705.6139 | 4.2815 | -45.3387 | 4.0916 | -45.1706 | 9.5254 | 4.1072 | 5.8428 | 4.3198
119 | B113 | IEEE 118 Bus Test Case | Line 32-113 | 230 | 0 | 0 | -1 | 282.298 | 0.70863 | 140.58 | 0.66749 | 141.0412 | 1.5766 | 4.1072 | 5.8428 | 4.3198
120 | B113 | IEEE 118 Bus Test Case | Line 17-113 | 230 | 0 | 0 | -1 | 1425.1182 | 3.5774 | 133.4909 | 3.4288 | 133.6224 | 7.9589 | 4.1072 | 5.8428 | 4.3198
121 | B31 | IEEE 118 Bus Test Case | Line 17-113 | 230 | 0 | 0 | -1 | 1632.7268 | 4.0985 | -42.0994 | 3.609 | -40.9692 | 9.616 | 3.6492 | 6.526 | 4.1474
122 | B31 | IEEE 118 Bus Test Case | Line 17-31 | 230 | 0 | 0 | -1 | 450.0322 | 1.1297 | 133.8206 | 1.1024 | 133.7146 | 2.6505 | 3.6492 | 6.526 | 4.1474
123 | B31 | IEEE 118 Bus Test Case | Line 31-32 | 230 | 0 | 0 | -1 | 414.6648 | 1.0409 | 136.9807 | 1.0064 | 136.8325 | 2.4422 | 3.6492 | 6.526 | 4.1474
124 | B31 | IEEE 118 Bus Test Case | Load 31 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6492 | 6.526 | 4.1474
125 | B31 | IEEE 118 Bus Test Case | Line 29-31 | 230 | 0 | 0 | -1 | 203.3358 | 0.51042 | 135.6693 | 0.49182 | 135.5269 | 1.1976 | 3.6492 | 6.526 | 4.1474
126 | B31 | IEEE 118 Bus Test Case | Tx 31-123 | 230 | 0 | 0 | -1 | 567.9566 | 1.4257 | 142.6063 | 1.0292 | 148.5836 | 3.345 | 3.6492 | 6.526 | 4.1474
127 | B32 | IEEE 118 Bus Test Case | Tx 31-123 | 230 | 0 | 0 | -1 | 1632.7698 | 4.0986 | -41.9463 | 3.8186 | -41.6918 | 9.1268 | 3.8416 | 5.4761 | 4.1354
128 | B32 | IEEE 118 Bus Test Case | Gen 32 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8416 | 5.4761 | 4.1354
129 | B32 | IEEE 118 Bus Test Case | Line 23-32 | 230 | 0 | 0 | -1 | 475.4002 | 1.1934 | 136.9346 | 1.138 | 136.7977 | 2.6574 | 3.8416 | 5.4761 | 4.1354
130 | B32 | IEEE 118 Bus Test Case | Line 27-32 | 230 | 0 | 0 | -1 | 290.6717 | 0.72965 | 140.427 | 0.67618 | 140.701 | 1.6248 | 3.8416 | 5.4761 | 4.1354
131 | B32 | IEEE 118 Bus Test Case | Line 31-32 | 230 | 0 | 0 | -1 | 412.1782 | 1.0347 | 141.3477 | 0.92101 | 142.5856 | 2.304 | 3.8416 | 5.4761 | 4.1354
132 | B32 | IEEE 118 Bus Test Case | Load 32 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8416 | 5.4761 | 4.1354
133 | B32 | IEEE 118 Bus Test Case | Line 32-114 | 230 | 0 | 0 | -1 | 152.805 | 0.38357 | 135.3886 | 0.35547 | 135.6626 | 0.85414 | 3.8416 | 5.4761 | 4.1354
134 | B32 | IEEE 118 Bus Test Case | Line 32-113 | 230 | 0 | 0 | -1 | 303.5172 | 0.76189 | 134.4021 | 0.73366 | 134.3597 | 1.6966 | 3.8416 | 5.4761 | 4.1354
135 | B37 | IEEE 118 Bus Test Case | Line 32-113 | 230 | 0 | 0 | -1 | 2134.9442 | 5.3592 | -51.2684 | 5.1801 | -50.9263 | 12.898 | 5.1948 | 8.0365 | 5.4343
136 | B37 | IEEE 118 Bus Test Case | Line 35-37 | 230 | 0 | 0 | -1 | 31.3348 | 0.078657 | 133.0435 | 0.07573 | 133.432 | 0.18931 | 5.1948 | 8.0365 | 5.4343
137 | B37 | IEEE 118 Bus Test Case | Line 37-40 | 230 | 0 | 0 | -1 | 123.6609 | 0.31042 | 129.4467 | 0.30087 | 129.7319 | 0.74708 | 5.1948 | 8.0365 | 5.4343
138 | B37 | IEEE 118 Bus Test Case | Shunt 37 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1948 | 8.0365 | 5.4343
139 | B37 | IEEE 118 Bus Test Case | Line 34-37 | 230 | 0 | 0 | -1 | 290.0481 | 0.72808 | 133.5603 | 0.70099 | 133.9488 | 1.7523 | 5.1948 | 8.0365 | 5.4343
140 | B37 | IEEE 118 Bus Test Case | Line 37-39 | 230 | 0 | 0 | -1 | 125.7186 | 0.31558 | 126.3048 | 0.30588 | 126.59 | 0.75951 | 5.1948 | 8.0365 | 5.4343
141 | B37 | IEEE 118 Bus Test Case | Tx 38-37 | 230 | 0 | 0 | -1 | 1375.443 | 3.4527 | 126.5639 | 3.3426 | 126.8995 | 8.3096 | 5.1948 | 8.0365 | 5.4343
142 | B37 | IEEE 118 Bus Test Case | Line 33-37 | 230 | 0 | 0 | -1 | 193.1579 | 0.48487 | 137.3764 | 0.46499 | 137.8919 | 1.1669 | 5.1948 | 8.0365 | 5.4343
143 | B38 | IEEE 118 Bus Test Case | Line 33-37 | 500 | 0 | 0 | -1 | 2537.4162 | 2.93 | -51.4469 | 2.8208 | -51.0829 | 7.1032 | 2.8297 | 4.2402 | 2.9732
144 | B38 | IEEE 118 Bus Test Case | Line 30-38 | 500 | 0 | 0 | -1 | 964.286 | 1.1135 | 129.6266 | 1.0627 | 130.1795 | 2.6994 | 2.8297 | 4.2402 | 2.9732
145 | B38 | IEEE 118 Bus Test Case | Line 38-65 | 500 | 0 | 0 | -1 | 903.5351 | 1.0433 | 126.1868 | 1.0161 | 126.3767 | 2.5293 | 2.8297 | 4.2402 | 2.9732
146 | B38 | IEEE 118 Bus Test Case | Tx 38-37 | 500 | 0 | 0 | -1 | 670.8106 | 0.77459 | 130.1964 | 0.7436 | 130.5836 | 1.8778 | 2.8297 | 4.2402 | 2.9732
147 | B110 | IEEE 118 Bus Test Case | Tx 38-37 | 230 | 0 | 0 | -1 | 1139.8589 | 2.8613 | -37.3941 | 2.4856 | -37.4931 | 6.4719 | 2.5164 | 3.6125 | 2.8891
148 | B110 | IEEE 118 Bus Test Case | Gen 110 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5164 | 3.6125 | 2.8891
149 | B110 | IEEE 118 Bus Test Case | Line 103-110 | 230 | 0 | 0 | -1 | 392.4999 | 0.98526 | 139.7288 | 0.9274 | 139.7675 | 2.2285 | 2.5164 | 3.6125 | 2.8891
150 | B110 | IEEE 118 Bus Test Case | Shunt 110 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5164 | 3.6125 | 2.8891
151 | B110 | IEEE 118 Bus Test Case | Load 110 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5164 | 3.6125 | 2.8891
152 | B110 | IEEE 118 Bus Test Case | Line 110-112 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5164 | 3.6125 | 2.8891
153 | B110 | IEEE 118 Bus Test Case | Line 110-111 | 230 | 0 | 0 | -1 | 441.7293 | 1.1088 | 143.7486 | 0.8303 | 143.6948 | 2.508 | 2.5164 | 3.6125 | 2.8891
154 | B110 | IEEE 118 Bus Test Case | Line 109-110 | 230 | 0 | 0 | -1 | 306.4059 | 0.76915 | 144.6429 | 0.72965 | 144.6363 | 1.7397 | 2.5164 | 3.6125 | 2.8891
155 | B109 | IEEE 118 Bus Test Case | Line 109-110 | 230 | 0 | 0 | -1 | 943.9105 | 2.3694 | -34.0862 | 2.1713 | -34.3953 | 4.9845 | 2.1875 | 3.097 | 2.3859
156 | B109 | IEEE 118 Bus Test Case | Load 109 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1875 | 3.097 | 2.3859
157 | B109 | IEEE 118 Bus Test Case | Line 108-109 | 230 | 0 | 0 | -1 | 473.3831 | 1.1883 | 144.6348 | 1.1252 | 144.5514 | 2.4998 | 2.1875 | 3.097 | 2.3859
158 | B109 | IEEE 118 Bus Test Case | Line 109-110 | 230 | 0 | 0 | -1 | 470.7639 | 1.1817 | 147.1999 | 1.0465 | 146.7372 | 2.486 | 2.1875 | 3.097 | 2.3859
159 | B88 | IEEE 118 Bus Test Case | Line 109-110 | 230 | 0 | 0 | -1 | 1398.1675 | 3.5097 | -37.4061 | 3.3423 | -37.3353 | 8.091 | 3.3561 | 4.8393 | 3.5475
160 | B88 | IEEE 118 Bus Test Case | Load 88 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3561 | 4.8393 | 3.5475
161 | B88 | IEEE 118 Bus Test Case | Line 85-88 | 230 | 0 | 0 | -1 | 457.2756 | 1.1479 | 139.9844 | 1.1035 | 139.9248 | 2.6462 | 3.3561 | 4.8393 | 3.5475
162 | B88 | IEEE 118 Bus Test Case | Line 88-89 | 230 | 0 | 0 | -1 | 941.5962 | 2.3636 | 143.8609 | 2.2407 | 144.0137 | 5.4489 | 3.3561 | 4.8393 | 3.5475
163 | B15 | IEEE 118 Bus Test Case | Line 88-89 | 230 | 0 | 0 | -1 | 2031.9606 | 5.1007 | -45.2394 | 4.8593 | -44.9942 | 11.3962 | 4.8791 | 6.9433 | 5.1472
164 | B15 | IEEE 118 Bus Test Case | Gen 15 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8791 | 6.9433 | 5.1472
165 | B15 | IEEE 118 Bus Test Case | Line 15-19 | 230 | 0 | 0 | -1 | 477.5753 | 1.1988 | 132.6119 | 1.1489 | 132.8428 | 2.6785 | 4.8791 | 6.9433 | 5.1472
166 | B15 | IEEE 118 Bus Test Case | Line 15-17 | 230 | 0 | 0 | -1 | 941.0283 | 2.3622 | 135.5165 | 2.2485 | 135.7663 | 5.2777 | 4.8791 | 6.9433 | 5.1472
167 | B15 | IEEE 118 Bus Test Case | Line 14-15 | 230 | 0 | 0 | -1 | 225.3127 | 0.56558 | 137.3065 | 0.52924 | 137.731 | 1.2637 | 4.8791 | 6.9433 | 5.1472
168 | B15 | IEEE 118 Bus Test Case | Line 13-15 | 230 | 0 | 0 | -1 | 180.0879 | 0.45206 | 136.2464 | 0.42454 | 136.5921 | 1.01 | 4.8791 | 6.9433 | 5.1472
169 | B15 | IEEE 118 Bus Test Case | Line 15-33 | 230 | 0 | 0 | -1 | 208.8592 | 0.52428 | 132.2391 | 0.51042 | 132.379 | 1.1714 | 4.8791 | 6.9433 | 5.1472
170 | B15 | IEEE 118 Bus Test Case | Load 15 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8791 | 6.9433 | 5.1472
171 | B100 | IEEE 118 Bus Test Case | Load 15 | 230 | 0 | 0 | -1 | 4109.6496 | 10.3161 | -41.9073 | 8.24 | -40.4633 | 25.6593 | 8.4104 | 19.7741 | 9.6811
172 | B100 | IEEE 118 Bus Test Case | Line 100-106 | 230 | 0 | 0 | -1 | 83.5385 | 0.2097 | 140.2524 | 0.16855 | 140.4691 | 0.52159 | 8.4104 | 19.7741 | 9.6811
173 | B100 | IEEE 118 Bus Test Case | Line 100-104 | 230 | 0 | 0 | -1 | 104.6203 | 0.26262 | 138.0604 | 0.20987 | 138.2767 | 0.65321 | 8.4104 | 19.7741 | 9.6811
174 | B100 | IEEE 118 Bus Test Case | Load 100 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4104 | 19.7741 | 9.6811
175 | B100 | IEEE 118 Bus Test Case | Line 92-100 | 230 | 0 | 0 | -1 | 185.263 | 0.46505 | 142.8882 | 0.44513 | 142.9232 | 1.1567 | 8.4104 | 19.7741 | 9.6811
176 | B100 | IEEE 118 Bus Test Case | Line 94-100 | 230 | 0 | 0 | -1 | 625.0435 | 1.569 | 139.914 | 1.5106 | 139.7746 | 3.9026 | 8.4104 | 19.7741 | 9.6811
177 | B100 | IEEE 118 Bus Test Case | Line 98-100 | 230 | 0 | 0 | -1 | 289.5642 | 0.72687 | 130.997 | 0.70361 | 130.749 | 1.8079 | 8.4104 | 19.7741 | 9.6811
178 | B100 | IEEE 118 Bus Test Case | Line 100-103 | 230 | 0 | 0 | -1 | 556.3982 | 1.3967 | 140.3239 | 1.0946 | 140.5117 | 3.474 | 8.4104 | 19.7741 | 9.6811
179 | B100 | IEEE 118 Bus Test Case | Line 100-101 | 230 | 0 | 0 | -1 | 183.3958 | 0.46036 | 141.9588 | 0.44065 | 141.9938 | 1.1451 | 8.4104 | 19.7741 | 9.6811
180 | B100 | IEEE 118 Bus Test Case | Line 99-100 | 230 | 0 | 0 | -1 | 288.1833 | 0.7234 | 133.3419 | 0.70026 | 133.0939 | 1.7993 | 8.4104 | 19.7741 | 9.6811
181 | B100 | IEEE 118 Bus Test Case | Tx 100-135 | 230 | 0 | 0 | -1 | 1798.7592 | 4.5153 | 137.684 | 2.9831 | 141.8009 | 11.2309 | 8.4104 | 19.7741 | 9.6811
182 | B14 | IEEE 118 Bus Test Case | Tx 100-135 | 230 | 0 | 0 | -1 | 1141.4669 | 2.8653 | -44.2742 | 2.738 | -44.1027 | 6.1777 | 2.7484 | 3.8965 | 2.8874
183 | B14 | IEEE 118 Bus Test Case | Line 14-15 | 230 | 0 | 0 | -1 | 331.5773 | 0.83233 | 134.3482 | 0.81063 | 134.4351 | 1.7945 | 2.7484 | 3.8965 | 2.8874
184 | B14 | IEEE 118 Bus Test Case | Load 14 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7484 | 3.8965 | 2.8874
185 | B14 | IEEE 118 Bus Test Case | Line 12-14 | 230 | 0 | 0 | -1 | 810.0246 | 2.0333 | 136.2896 | 1.9277 | 136.5122 | 4.3839 | 2.7484 | 3.8965 | 2.8874
186 | B29 | IEEE 118 Bus Test Case | Line 12-14 | 230 | 0 | 0 | -1 | 1190.5734 | 2.9886 | -40.5996 | 2.7434 | -40.0083 | 6.6553 | 2.7635 | 4.0391 | 3.0155
187 | B29 | IEEE 118 Bus Test Case | Line 29-31 | 230 | 0 | 0 | -1 | 909.9652 | 2.2842 | 140.4282 | 2.0683 | 141.2706 | 5.0867 | 2.7635 | 4.0391 | 3.0155
188 | B29 | IEEE 118 Bus Test Case | Line 28-29 | 230 | 0 | 0 | -1 | 281.2286 | 0.70595 | 136.0734 | 0.67717 | 136.0829 | 1.5721 | 2.7635 | 4.0391 | 3.0155
189 | B29 | IEEE 118 Bus Test Case | Load 29 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7635 | 4.0391 | 3.0155
190 | B104 | IEEE 118 Bus Test Case | Load 29 | 230 | 0 | 0 | -1 | 1331.4776 | 3.3423 | -36.6303 | 3.0602 | -36.4752 | 7.326 | 3.0834 | 4.3874 | 3.3701
191 | B104 | IEEE 118 Bus Test Case | Gen 104 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0834 | 4.3874 | 3.3701
192 | B104 | IEEE 118 Bus Test Case | Load 104 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0834 | 4.3874 | 3.3701
193 | B104 | IEEE 118 Bus Test Case | Line 104-105 | 230 | 0 | 0 | -1 | 586.3109 | 1.4718 | 144.5542 | 1.3401 | 144.656 | 3.226 | 3.0834 | 4.3874 | 3.3701
194 | B104 | IEEE 118 Bus Test Case | Line 100-104 | 230 | 0 | 0 | -1 | 371.268 | 0.93196 | 140.8101 | 0.86932 | 141.0018 | 2.0428 | 3.0834 | 4.3874 | 3.3701
195 | B104 | IEEE 118 Bus Test Case | Line 103-104 | 230 | 0 | 0 | -1 | 374.421 | 0.93988 | 144.0524 | 0.852 | 144.3191 | 2.0601 | 3.0834 | 4.3874 | 3.3701
196 | B33 | IEEE 118 Bus Test Case | Line 103-104 | 230 | 0 | 0 | -1 | 956.2692 | 2.4004 | -45.6554 | 2.3567 | -45.5459 | 5.0681 | 2.3603 | 3.3407 | 2.4174
197 | B33 | IEEE 118 Bus Test Case | Load 33 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3603 | 3.3407 | 2.4174
198 | B33 | IEEE 118 Bus Test Case | Line 15-33 | 230 | 0 | 0 | -1 | 491.9938 | 1.235 | 135.7258 | 1.2089 | 135.8645 | 2.6075 | 2.3603 | 3.3407 | 2.4174
199 | B33 | IEEE 118 Bus Test Case | Line 33-37 | 230 | 0 | 0 | -1 | 464.5697 | 1.1662 | 132.8818 | 1.1486 | 132.9697 | 2.4621 | 2.3603 | 3.3407 | 2.4174
200 | B86 | IEEE 118 Bus Test Case | Line 33-37 | 230 | 0 | 0 | -1 | 757.4325 | 1.9013 | -36.7672 | 1.7794 | -36.5908 | 4.2798 | 1.7894 | 2.5911 | 1.9193
201 | B86 | IEEE 118 Bus Test Case | Line 85-86 | 230 | 0 | 0 | -1 | 487.5217 | 1.2238 | 143.9643 | 1.2068 | 143.9311 | 2.7547 | 1.7894 | 2.5911 | 1.9193
202 | B86 | IEEE 118 Bus Test Case | Line 86-87 | 230 | 0 | 0 | -1 | 270.0223 | 0.67781 | 141.9119 | 0.57273 | 142.3095 | 1.5257 | 1.7894 | 2.5911 | 1.9193
203 | B86 | IEEE 118 Bus Test Case | Load 86 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7894 | 2.5911 | 1.9193
204 | B3 | IEEE 118 Bus Test Case | Load 86 | 230 | 0 | 0 | -1 | 1179.0429 | 2.9597 | -46.0264 | 2.8205 | -45.8882 | 6.6632 | 2.8319 | 4.0336 | 2.9877
205 | B3 | IEEE 118 Bus Test Case | Line 1-3 | 230 | 0 | 0 | -1 | 271.5482 | 0.68165 | 136.4431 | 0.64543 | 136.6895 | 1.5346 | 2.8319 | 4.0336 | 2.9877
206 | B3 | IEEE 118 Bus Test Case | Line 3-5 | 230 | 0 | 0 | -1 | 554.3456 | 1.3915 | 131.5298 | 1.3359 | 131.5809 | 3.1328 | 2.8319 | 4.0336 | 2.9877
207 | B3 | IEEE 118 Bus Test Case | Line 3-12 | 230 | 0 | 0 | -1 | 354.1067 | 0.88889 | 135.9054 | 0.84167 | 136.1518 | 2.0012 | 2.8319 | 4.0336 | 2.9877
208 | B3 | IEEE 118 Bus Test Case | Load 3 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8319 | 4.0336 | 2.9877
209 | B72 | IEEE 118 Bus Test Case | Load 3 | 230 | 0 | 0 | -1 | 642.388 | 1.6125 | -45.0582 | 1.5942 | -45.0661 | 3.4172 | 1.5957 | 2.2582 | 1.6241
210 | B72 | IEEE 118 Bus Test Case | Gen 72 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5957 | 2.2582 | 1.6241
211 | B72 | IEEE 118 Bus Test Case | Line 71-72 | 230 | 0 | 0 | -1 | 324.2596 | 0.81396 | 131.8412 | 0.80726 | 131.8471 | 1.7249 | 1.5957 | 2.2582 | 1.6241
212 | B72 | IEEE 118 Bus Test Case | Line 24-72 | 230 | 0 | 0 | -1 | 319.0854 | 0.80097 | 138.0927 | 0.78935 | 138.0908 | 1.6974 | 1.5957 | 2.2582 | 1.6241
213 | B99 | IEEE 118 Bus Test Case | Line 24-72 | 230 | 0 | 0 | -1 | 1355.2087 | 3.4019 | -41.1338 | 3.2222 | -41.0136 | 7.5879 | 3.237 | 4.6119 | 3.4327
214 | B99 | IEEE 118 Bus Test Case | Gen 99 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.237 | 4.6119 | 3.4327
215 | B99 | IEEE 118 Bus Test Case | Line 99-100 | 230 | 0 | 0 | -1 | 915.52 | 2.2982 | 141.5055 | 2.1456 | 141.8749 | 5.126 | 3.237 | 4.6119 | 3.4327
216 | B99 | IEEE 118 Bus Test Case | Line 80-99 | 230 | 0 | 0 | -1 | 442.672 | 1.1112 | 133.4012 | 1.0848 | 133.2661 | 2.4785 | 3.237 | 4.6119 | 3.4327
217 | B90 | IEEE 118 Bus Test Case | Line 80-99 | 230 | 0 | 0 | -1 | 1316.4548 | 3.3046 | -34.558 | 3.1435 | -34.6228 | 7.3251 | 3.1567 | 4.4947 | 3.3336
218 | B90 | IEEE 118 Bus Test Case | Gen 90 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1567 | 4.4947 | 3.3336
219 | B90 | IEEE 118 Bus Test Case | Line 89-90 C1 | 230 | 0 | 0 | -1 | 347.6101 | 0.87258 | 146.4447 | 0.82791 | 146.3965 | 1.9342 | 3.1567 | 4.4947 | 3.3336
220 | B90 | IEEE 118 Bus Test Case | Line 89-90 C2 | 230 | 0 | 0 | -1 | 661.3178 | 1.6601 | 144.4663 | 1.5751 | 144.418 | 3.6797 | 3.1567 | 4.4947 | 3.3336
221 | B90 | IEEE 118 Bus Test Case | Line 90-91 | 230 | 0 | 0 | -1 | 307.7196 | 0.77244 | 146.4063 | 0.74091 | 146.2774 | 1.7122 | 3.1567 | 4.4947 | 3.3336
222 | B90 | IEEE 118 Bus Test Case | Load 90 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1567 | 4.4947 | 3.3336
223 | B91 | IEEE 118 Bus Test Case | Load 90 | 230 | 0 | 0 | -1 | 1019.9738 | 2.5604 | -34.1469 | 2.4703 | -34.2694 | 5.446 | 2.4777 | 3.5089 | 2.579
224 | B91 | IEEE 118 Bus Test Case | Gen 91 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4777 | 3.5089 | 2.579
225 | B91 | IEEE 118 Bus Test Case | Line 90-91 | 230 | 0 | 0 | -1 | 497.3566 | 1.2485 | 146.2825 | 1.201 | 146.1852 | 2.6556 | 2.4777 | 3.5089 | 2.579
226 | B91 | IEEE 118 Bus Test Case | Line 91-92 | 230 | 0 | 0 | -1 | 522.6445 | 1.312 | 145.4445 | 1.2694 | 145.3006 | 2.7906 | 2.4777 | 3.5089 | 2.579
227 | B42 | IEEE 118 Bus Test Case | Line 91-92 | 230 | 0 | 0 | -1 | 957.6053 | 2.4038 | -48.5266 | 2.3559 | -48.2954 | 5.1539 | 2.3598 | 3.3434 | 2.4219
228 | B42 | IEEE 118 Bus Test Case | Line 40-42 | 230 | 0 | 0 | -1 | 205.4731 | 0.51578 | 134.0202 | 0.50935 | 134.1542 | 1.1059 | 2.3598 | 3.3434 | 2.4219
229 | B42 | IEEE 118 Bus Test Case | Load 42 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3598 | 3.3434 | 2.4219
230 | B42 | IEEE 118 Bus Test Case | Line 42-49 C1 | 230 | 0 | 0 | -1 | 274.7097 | 0.68958 | 129.8893 | 0.67197 | 130.1724 | 1.4785 | 2.3598 | 3.3434 | 2.4219
231 | B42 | IEEE 118 Bus Test Case | Line 41-42 | 230 | 0 | 0 | -1 | 203.2159 | 0.51012 | 133.1819 | 0.50376 | 133.316 | 1.0937 | 2.3598 | 3.3434 | 2.4219
232 | B42 | IEEE 118 Bus Test Case | Line 42-49 C2 | 230 | 0 | 0 | -1 | 274.7097 | 0.68958 | 129.8893 | 0.67197 | 130.1724 | 1.4785 | 2.3598 | 3.3434 | 2.4219
233 | B7 | IEEE 118 Bus Test Case | Line 42-49 C2 | 230 | 0 | 0 | -1 | 1681.3817 | 4.2206 | -47.6347 | 3.9248 | -47.2704 | 9.9515 | 3.9491 | 5.7669 | 4.2725
234 | B7 | IEEE 118 Bus Test Case | Line 7-12 | 230 | 0 | 0 | -1 | 1078.1291 | 2.7063 | 133.3702 | 2.4895 | 133.923 | 6.381 | 3.9491 | 5.7669 | 4.2725
235 | B7 | IEEE 118 Bus Test Case | Load 7 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9491 | 5.7669 | 4.2725
236 | B7 | IEEE 118 Bus Test Case | Line 6-7 | 230 | 0 | 0 | -1 | 603.7146 | 1.5155 | 130.5704 | 1.4368 | 130.6615 | 3.5732 | 3.9491 | 5.7669 | 4.2725
237 | B21 | IEEE 118 Bus Test Case | Line 6-7 | 230 | 0 | 0 | -1 | 652.41 | 1.6377 | -46.6158 | 1.6103 | -46.5119 | 3.5995 | 1.6125 | 2.2855 | 1.6515
238 | B21 | IEEE 118 Bus Test Case | Line 20-21 | 230 | 0 | 0 | -1 | 349.8721 | 0.87826 | 130.3653 | 0.86545 | 130.4622 | 1.9303 | 1.6125 | 2.2855 | 1.6515
239 | B21 | IEEE 118 Bus Test Case | Line 21-22 | 230 | 0 | 0 | -1 | 303.5831 | 0.76206 | 136.864 | 0.74745 | 136.9922 | 1.675 | 1.6125 | 2.2855 | 1.6515
240 | B21 | IEEE 118 Bus Test Case | Load 21 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6125 | 2.2855 | 1.6515
241 | B64 | IEEE 118 Bus Test Case | Load 21 | 500 | 0 | 0 | -1 | 4378.8847 | 5.0563 | -55.4777 | 4.5879 | -54.3478 | 13.1265 | 4.6264 | 8.7832 | 5.1952
242 | B64 | IEEE 118 Bus Test Case | Tx 64-61 | 500 | 0 | 0 | -1 | 1109.0364 | 1.2806 | 123.0255 | 1.1136 | 124.6242 | 3.3245 | 4.6264 | 8.7832 | 5.1952
243 | B64 | IEEE 118 Bus Test Case | Line 63-64 | 500 | 0 | 0 | -1 | 950.7411 | 1.0978 | 120.4844 | 0.96501 | 122.1699 | 2.85 | 4.6264 | 8.7832 | 5.1952
244 | B64 | IEEE 118 Bus Test Case | Line 64-65 | 500 | 0 | 0 | -1 | 2323.826 | 2.6833 | 126.8879 | 2.5125 | 127.4448 | 6.9661 | 4.6264 | 8.7832 | 5.1952
245 | B81 | IEEE 118 Bus Test Case | Line 64-65 | 500 | 0 | 0 | -1 | 4528.6619 | 5.2292 | -54.4582 | 4.8642 | -53.8271 | 13.7254 | 4.8942 | 9.5123 | 5.3948
246 | B81 | IEEE 118 Bus Test Case | Line 68-81 | 500 | 0 | 0 | -1 | 2714.6686 | 3.1346 | 124.9425 | 2.9312 | 125.2768 | 8.2276 | 4.8942 | 9.5123 | 5.3948
247 | B81 | IEEE 118 Bus Test Case | Tx 81-80 | 500 | 0 | 0 | -1 | 1814.3639 | 2.095 | 126.4384 | 1.9339 | 127.5313 | 5.499 | 4.8942 | 9.5123 | 5.3948
248 | B6 | IEEE 118 Bus Test Case | Tx 81-80 | 230 | 0 | 0 | -1 | 1602.5951 | 4.0229 | -48.3064 | 3.769 | -48.0126 | 9.4974 | 3.7898 | 5.5053 | 4.0727
249 | B6 | IEEE 118 Bus Test Case | Gen 6 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7898 | 5.5053 | 4.0727
250 | B6 | IEEE 118 Bus Test Case | Load 6 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7898 | 5.5053 | 4.0727
251 | B6 | IEEE 118 Bus Test Case | Line 5-6 | 230 | 0 | 0 | -1 | 814.1867 | 2.0438 | 130.5617 | 1.9384 | 130.6733 | 4.8251 | 3.7898 | 5.5053 | 4.0727
252 | B6 | IEEE 118 Bus Test Case | Line 6-7 | 230 | 0 | 0 | -1 | 788.7313 | 1.9799 | 132.862 | 1.8317 | 133.3782 | 4.6742 | 3.7898 | 5.5053 | 4.0727
253 | B116 | IEEE 118 Bus Test Case | Line 6-7 | 500 | 0 | 0 | -1 | 5875.5905 | 6.7845 | -54.6705 | 6.1557 | -54.031 | 17.623 | 6.2073 | 11.1173 | 6.9722
254 | B116 | IEEE 118 Bus Test Case | Gen 116 | 500 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2073 | 11.1173 | 6.9722
255 | B116 | IEEE 118 Bus Test Case | Line 68-116 | 500 | 0 | 0 | -1 | 5875.5905 | 6.7845 | 125.3295 | 6.1557 | 125.969 | 17.623 | 6.2073 | 11.1173 | 6.9722
256 | B19 | IEEE 118 Bus Test Case | Line 68-116 | 230 | 0 | 0 | -1 | 1706.0773 | 4.2826 | -45.4895 | 4.1197 | -45.2587 | 9.4941 | 4.1331 | 5.8726 | 4.3203
257 | B19 | IEEE 118 Bus Test Case | Gen 19 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1331 | 5.8726 | 4.3203
258 | B19 | IEEE 118 Bus Test Case | Line 19-20 | 230 | 0 | 0 | -1 | 163.6314 | 0.41075 | 134.6944 | 0.39433 | 134.9715 | 0.91059 | 4.1331 | 5.8726 | 4.3203
259 | B19 | IEEE 118 Bus Test Case | Line 19-34 | 230 | 0 | 0 | -1 | 237.6941 | 0.59666 | 133.8789 | 0.58239 | 134.0133 | 1.3227 | 4.1331 | 5.8726 | 4.3203
260 | B19 | IEEE 118 Bus Test Case | Load 19 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1331 | 5.8726 | 4.3203
261 | B19 | IEEE 118 Bus Test Case | Line 18-19 | 230 | 0 | 0 | -1 | 512.607 | 1.2868 | 132.5174 | 1.2347 | 132.7627 | 2.8526 | 4.1331 | 5.8726 | 4.3203
262 | B19 | IEEE 118 Bus Test Case | Line 15-19 | 230 | 0 | 0 | -1 | 792.7204 | 1.9899 | 135.9506 | 1.9097 | 136.1949 | 4.4114 | 4.1331 | 5.8726 | 4.3203
263 | B82 | IEEE 118 Bus Test Case | Line 15-19 | 230 | 0 | 0 | -1 | 2032.7375 | 5.1026 | -39.2399 | 4.911 | -39.2603 | 10.6753 | 4.9267 | 6.9717 | 5.1372
264 | B82 | IEEE 118 Bus Test Case | Line 82-83 | 230 | 0 | 0 | -1 | 419.9921 | 1.0543 | 149.2216 | 1.0112 | 149.4048 | 2.2057 | 4.9267 | 6.9717 | 5.1372
265 | B82 | IEEE 118 Bus Test Case | Load 82 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9267 | 6.9717 | 5.1372
266 | B82 | IEEE 118 Bus Test Case | Line 77-82 | 230 | 0 | 0 | -1 | 788.7726 | 1.98 | 137.1238 | 1.9181 | 136.9942 | 4.1424 | 4.9267 | 6.9717 | 5.1372
267 | B82 | IEEE 118 Bus Test Case | Shunt 82 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9267 | 6.9717 | 5.1372
268 | B82 | IEEE 118 Bus Test Case | Line 82-96 | 230 | 0 | 0 | -1 | 830.2159 | 2.084 | 139.9476 | 1.9975 | 139.964 | 4.36 | 4.9267 | 6.9717 | 5.1372
269 | B27 | IEEE 118 Bus Test Case | Line 82-96 | 230 | 0 | 0 | -1 | 1396.9224 | 3.5066 | -42.9618 | 3.2916 | -42.7619 | 7.858 | 3.3093 | 4.7177 | 3.5391
270 | B27 | IEEE 118 Bus Test Case | Gen 27 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3093 | 4.7177 | 3.5391
271 | B27 | IEEE 118 Bus Test Case | Line 27-32 | 230 | 0 | 0 | -1 | 426.6676 | 1.071 | 138.5232 | 1.0097 | 138.7137 | 2.4001 | 3.3093 | 4.7177 | 3.5391
272 | B27 | IEEE 118 Bus Test Case | Line 25-27 | 230 | 0 | 0 | -1 | 510.1418 | 1.2806 | 136.9305 | 1.2095 | 136.866 | 2.8696 | 3.3093 | 4.7177 | 3.5391
273 | B27 | IEEE 118 Bus Test Case | Line 27-115 | 230 | 0 | 0 | -1 | 224.2975 | 0.56304 | 133.4848 | 0.5308 | 133.6753 | 1.2617 | 3.3093 | 4.7177 | 3.5391
274 | B27 | IEEE 118 Bus Test Case | Load 27 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3093 | 4.7177 | 3.5391
275 | B27 | IEEE 118 Bus Test Case | Line 27-28 | 230 | 0 | 0 | -1 | 236.4215 | 0.59347 | 137.9597 | 0.54318 | 138.8037 | 1.3299 | 3.3093 | 4.7177 | 3.5391
276 | B18 | IEEE 118 Bus Test Case | Line 27-28 | 230 | 0 | 0 | -1 | 1587.5773 | 3.9852 | -46.4136 | 3.8383 | -46.1734 | 8.9861 | 3.8503 | 5.4879 | 4.0233
277 | B18 | IEEE 118 Bus Test Case | Gen 18 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8503 | 5.4879 | 4.0233
278 | B18 | IEEE 118 Bus Test Case | Line 17-18 | 230 | 0 | 0 | -1 | 986.8571 | 2.4772 | 133.9822 | 2.3827 | 134.2323 | 5.5858 | 3.8503 | 5.4879 | 4.0233
279 | B18 | IEEE 118 Bus Test Case | Line 18-19 | 230 | 0 | 0 | -1 | 600.7824 | 1.5081 | 132.9362 | 1.4557 | 133.1625 | 3.4006 | 3.8503 | 5.4879 | 4.0233
280 | B18 | IEEE 118 Bus Test Case | Load 18 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8503 | 5.4879 | 4.0233
281 | B115 | IEEE 118 Bus Test Case | Load 18 | 230 | 0 | 0 | -1 | 1056.0807 | 2.651 | -42.6961 | 2.5296 | -42.4972 | 5.8872 | 2.5396 | 3.6095 | 2.6745
282 | B115 | IEEE 118 Bus Test Case | Line 114-115 | 230 | 0 | 0 | -1 | 570.2692 | 1.4315 | 136.4704 | 1.3675 | 136.6638 | 3.179 | 2.5396 | 3.6095 | 2.6745
283 | B115 | IEEE 118 Bus Test Case | Line 27-115 | 230 | 0 | 0 | -1 | 485.9426 | 1.2198 | 138.282 | 1.1625 | 138.4897 | 2.7089 | 2.5396 | 3.6095 | 2.6745
284 | B115 | IEEE 118 Bus Test Case | Load 115 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5396 | 3.6095 | 2.6745
285 | B28 | IEEE 118 Bus Test Case | Load 115 | 230 | 0 | 0 | -1 | 947.5669 | 2.3786 | -41.7891 | 2.2569 | -41.4941 | 5.2583 | 2.2669 | 3.2288 | 2.3992
286 | B28 | IEEE 118 Bus Test Case | Load 28 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2669 | 3.2288 | 2.3992
287 | B28 | IEEE 118 Bus Test Case | Line 27-28 | 230 | 0 | 0 | -1 | 520.9492 | 1.3077 | 137.0121 | 1.2572 | 137.0781 | 2.8909 | 2.2669 | 3.2288 | 2.3992
288 | B28 | IEEE 118 Bus Test Case | Line 28-29 | 230 | 0 | 0 | -1 | 426.8709 | 1.0715 | 139.6738 | 1.0007 | 140.2999 | 2.3688 | 2.2669 | 3.2288 | 2.3992
289 | B66 | IEEE 118 Bus Test Case | Line 28-29 | 230 | 0 | 0 | -1 | 8418.56 | 21.1324 | -54.9156 | 17.6155 | -53.9401 | 56.2165 | 17.9042 | 38.7377 | 21.9509
290 | B66 | IEEE 118 Bus Test Case | Line 66-67 | 230 | 0 | 0 | -1 | 186.8611 | 0.46906 | 126.4583 | 0.41242 | 127.4457 | 1.2478 | 17.9042 | 38.7377 | 21.9509
291 | B66 | IEEE 118 Bus Test Case | Load 66 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 17.9042 | 38.7377 | 21.9509
292 | B66 | IEEE 118 Bus Test Case | Line 49-66 C1 | 230 | 0 | 0 | -1 | 598.3801 | 1.5021 | 126.168 | 1.2847 | 127.3765 | 3.9958 | 17.9042 | 38.7377 | 21.9509
293 | B66 | IEEE 118 Bus Test Case | Line 49-66 C2 | 230 | 0 | 0 | -1 | 598.3801 | 1.5021 | 126.168 | 1.2847 | 127.3765 | 3.9958 | 17.9042 | 38.7377 | 21.9509
294 | B66 | IEEE 118 Bus Test Case | Tx 65-66 | 230 | 0 | 0 | -1 | 4139.5493 | 10.3912 | 124.197 | 9.1846 | 125.1133 | 27.6426 | 17.9042 | 38.7377 | 21.9509
295 | B66 | IEEE 118 Bus Test Case | Line 62-66 | 230 | 0 | 0 | -1 | 188.2682 | 0.47259 | 127.2844 | 0.41552 | 128.2718 | 1.2572 | 17.9042 | 38.7377 | 21.9509
296 | B66 | IEEE 118 Bus Test Case | Tx 66-130 | 230 | 0 | 0 | -1 | 2708.1877 | 6.7981 | 125.7142 | 5.0363 | 126.8186 | 18.0844 | 17.9042 | 38.7377 | 21.9509
297 | B65 | IEEE 118 Bus Test Case | Tx 66-130 | 500 | 0 | 0 | -1 | 10018.8169 | 11.5687 | -54.7647 | 9.6649 | -53.7078 | 30.8531 | 9.8211 | 20.4011 | 12.0363
298 | B65 | IEEE 118 Bus Test Case | Line 65-68 | 500 | 0 | 0 | -1 | 2458.0614 | 2.8383 | 124.748 | 2.5749 | 125.3287 | 7.5696 | 9.8211 | 20.4011 | 12.0363
299 | B65 | IEEE 118 Bus Test Case | Tx 65-66 | 500 | 0 | 0 | -1 | 3222.3683 | 3.7209 | 124.0639 | 3.0299 | 125.2207 | 9.9233 | 9.8211 | 20.4011 | 12.0363
300 | B65 | IEEE 118 Bus Test Case | Line 38-65 | 500 | 0 | 0 | -1 | 537.9902 | 0.62122 | 125.7864 | 0.59243 | 126.364 | 1.6568 | 9.8211 | 20.4011 | 12.0363
301 | B65 | IEEE 118 Bus Test Case | Line 64-65 | 500 | 0 | 0 | -1 | 997.3637 | 1.1517 | 119.0671 | 0.99144 | 120.2467 | 3.0714 | 9.8211 | 20.4011 | 12.0363
302 | B65 | IEEE 118 Bus Test Case | Tx 65-129 | 500 | 0 | 0 | -1 | 2815.929 | 3.2516 | 129.0791 | 2.4909 | 130.9815 | 8.6717 | 9.8211 | 20.4011 | 12.0363
303 | B16 | IEEE 118 Bus Test Case | Tx 65-129 | 230 | 0 | 0 | -1 | 1130.422 | 2.8376 | -45.6502 | 2.7196 | -45.4295 | 6.2939 | 2.7293 | 3.8787 | 2.8626
304 | B16 | IEEE 118 Bus Test Case | Line 12-16 | 230 | 0 | 0 | -1 | 725.0488 | 1.82 | 134.7103 | 1.729 | 134.9993 | 4.0369 | 2.7293 | 3.8787 | 2.8626
305 | B16 | IEEE 118 Bus Test Case | Load 16 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7293 | 3.8787 | 2.8626
306 | B16 | IEEE 118 Bus Test Case | Line 16-17 | 230 | 0 | 0 | -1 | 405.4132 | 1.0177 | 133.7051 | 0.99073 | 133.8223 | 2.2572 | 2.7293 | 3.8787 | 2.8626
307 | B45 | IEEE 118 Bus Test Case | Line 16-17 | 230 | 0 | 0 | -1 | 1067.2304 | 2.679 | -46.3885 | 2.5624 | -46.0859 | 5.5585 | 2.5719 | 3.6435 | 2.6965
308 | B45 | IEEE 118 Bus Test Case | Load 45 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5719 | 3.6435 | 2.6965
309 | B45 | IEEE 118 Bus Test Case | Shunt 45 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5719 | 3.6435 | 2.6965
310 | B45 | IEEE 118 Bus Test Case | Line 45-46 | 230 | 0 | 0 | -1 | 456.9362 | 1.147 | 131.8059 | 1.0723 | 132.2731 | 2.3799 | 2.5719 | 3.6435 | 2.6965
311 | B45 | IEEE 118 Bus Test Case | Line 45-49 | 230 | 0 | 0 | -1 | 447.6271 | 1.1236 | 136.6093 | 1.0865 | 136.7914 | 2.3314 | 2.5719 | 3.6435 | 2.6965
312 | B45 | IEEE 118 Bus Test Case | Line 44-45 | 230 | 0 | 0 | -1 | 163.7547 | 0.41106 | 130.4565 | 0.40606 | 130.5491 | 0.85289 | 2.5719 | 3.6435 | 2.6965
313 | B71 | IEEE 118 Bus Test Case | Line 44-45 | 230 | 0 | 0 | -1 | 1090.6538 | 2.7378 | -46.4762 | 2.693 | -46.4367 | 5.8531 | 2.6967 | 3.827 | 2.7581
314 | B71 | IEEE 118 Bus Test Case | Line 71-73 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6967 | 3.827 | 2.7581
315 | B71 | IEEE 118 Bus Test Case | Line 70-71 | 230 | 0 | 0 | -1 | 915.725 | 2.2987 | 132.1886 | 2.2607 | 132.2147 | 4.9144 | 2.6967 | 3.827 | 2.7581
316 | B71 | IEEE 118 Bus Test Case | Line 71-72 | 230 | 0 | 0 | -1 | 176.4723 | 0.44298 | 140.4688 | 0.43621 | 140.5692 | 0.94706 | 2.6967 | 3.827 | 2.7581
317 | B62 | IEEE 118 Bus Test Case | Line 71-72 | 230 | 0 | 0 | -1 | 2507.7084 | 6.2949 | -51.7421 | 5.8814 | -51.2396 | 14.8541 | 5.9154 | 8.675 | 6.3726
318 | B62 | IEEE 118 Bus Test Case | Gen 62 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9154 | 8.675 | 6.3726
319 | B62 | IEEE 118 Bus Test Case | Line 61-62 | 230 | 0 | 0 | -1 | 1089.6435 | 2.7352 | 126.5131 | 2.5242 | 127.0365 | 6.4544 | 5.9154 | 8.675 | 6.3726
320 | B62 | IEEE 118 Bus Test Case | Line 62-66 | 230 | 0 | 0 | -1 | 397.4401 | 0.99766 | 132.9524 | 0.95528 | 133.2501 | 2.3542 | 5.9154 | 8.675 | 6.3726
321 | B62 | IEEE 118 Bus Test Case | Load 62 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9154 | 8.675 | 6.3726
322 | B62 | IEEE 118 Bus Test Case | Line 62-67 | 230 | 0 | 0 | -1 | 394.4697 | 0.99021 | 132.1263 | 0.94814 | 132.424 | 2.3366 | 5.9154 | 8.675 | 6.3726
323 | B62 | IEEE 118 Bus Test Case | Line 60-62 | 230 | 0 | 0 | -1 | 629.4282 | 1.58 | 125.8937 | 1.461 | 126.4291 | 3.7283 | 5.9154 | 8.675 | 6.3726
324 | B51 | IEEE 118 Bus Test Case | Line 60-62 | 230 | 0 | 0 | -1 | 1164.2965 | 2.9226 | -48.0955 | 2.8008 | -47.6464 | 5.9653 | 2.8108 | 3.9782 | 2.9405
325 | B51 | IEEE 118 Bus Test Case | Line 51-58 | 230 | 0 | 0 | -1 | 379.6136 | 0.95291 | 129.3696 | 0.90863 | 129.856 | 1.945 | 2.8108 | 3.9782 | 2.9405
326 | B51 | IEEE 118 Bus Test Case | Load 51 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8108 | 3.9782 | 2.9405
327 | B51 | IEEE 118 Bus Test Case | Line 49-51 | 230 | 0 | 0 | -1 | 596.9158 | 1.4984 | 136.4237 | 1.4438 | 136.7779 | 3.0583 | 2.8108 | 3.9782 | 2.9405
328 | B51 | IEEE 118 Bus Test Case | Line 51-52 | 230 | 0 | 0 | -1 | 192.3865 | 0.48293 | 122.8598 | 0.45922 | 123.3609 | 0.9857 | 2.8108 | 3.9782 | 2.9405
329 | B4 | IEEE 118 Bus Test Case | Line 51-52 | 230 | 0 | 0 | -1 | 2130.9308 | 5.3491 | -49.9432 | 4.9565 | -49.6209 | 13.1479 | 4.9887 | 7.6756 | 5.4364
330 | B4 | IEEE 118 Bus Test Case | Gen 4 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9887 | 7.6756 | 5.4364
331 | B4 | IEEE 118 Bus Test Case | Load 4 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9887 | 7.6756 | 5.4364
332 | B4 | IEEE 118 Bus Test Case | Line 4-5 | 230 | 0 | 0 | -1 | 1751.7778 | 4.3973 | 128.9618 | 4.0924 | 129.2237 | 10.8085 | 4.9887 | 7.6756 | 5.4364
333 | B4 | IEEE 118 Bus Test Case | Line 4-11 | 230 | 0 | 0 | -1 | 380.9468 | 0.95626 | 135.0985 | 0.8688 | 135.8297 | 2.3505 | 4.9887 | 7.6756 | 5.4364
334 | B39 | IEEE 118 Bus Test Case | Line 4-11 | 230 | 0 | 0 | -1 | 986.269 | 2.4758 | -47.3681 | 2.4374 | -47.2286 | 5.2921 | 2.4405 | 3.4563 | 2.4941
335 | B39 | IEEE 118 Bus Test Case | Line 37-39 | 230 | 0 | 0 | -1 | 554.3278 | 1.3915 | 133.5791 | 1.3708 | 133.7083 | 2.9744 | 2.4405 | 3.4563 | 2.4941
336 | B39 | IEEE 118 Bus Test Case | Load 39 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4405 | 3.4563 | 2.4941
337 | B39 | IEEE 118 Bus Test Case | Line 39-40 | 230 | 0 | 0 | -1 | 432.1141 | 1.0847 | 131.4168 | 1.067 | 131.5678 | 2.3186 | 2.4405 | 3.4563 | 2.4941
338 | B5 | IEEE 118 Bus Test Case | Line 39-40 | 230 | 0 | 0 | -1 | 2412.689 | 6.0564 | -50.683 | 5.5621 | -50.2711 | 15.2615 | 5.6027 | 9.2876 | 6.1782
339 | B5 | IEEE 118 Bus Test Case | Tx 8-5 | 230 | 0 | 0 | -1 | 1451.9553 | 3.6447 | 125.6025 | 3.4254 | 125.7469 | 9.1843 | 5.6027 | 9.2876 | 6.1782
340 | B5 | IEEE 118 Bus Test Case | Line 5-6 | 230 | 0 | 0 | -1 | 270.5333 | 0.6791 | 133.1736 | 0.60026 | 134.3921 | 1.7113 | 5.6027 | 9.2876 | 6.1782
341 | B5 | IEEE 118 Bus Test Case | Shunt 5 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6027 | 9.2876 | 6.1782
342 | B5 | IEEE 118 Bus Test Case | Line 4-5 | 230 | 0 | 0 | -1 | 259.9389 | 0.6525 | 135.9476 | 0.5812 | 137.0665 | 1.6442 | 5.6027 | 9.2876 | 6.1782
343 | B5 | IEEE 118 Bus Test Case | Line 3-5 | 230 | 0 | 0 | -1 | 144.2077 | 0.36199 | 134.2679 | 0.31997 | 135.4863 | 0.91219 | 5.6027 | 9.2876 | 6.1782
344 | B5 | IEEE 118 Bus Test Case | Line 5-11 | 230 | 0 | 0 | -1 | 293.8981 | 0.73775 | 135.8439 | 0.65713 | 136.9628 | 1.8591 | 5.6027 | 9.2876 | 6.1782
345 | B8 | IEEE 118 Bus Test Case | Line 5-11 | 500 | 0 | 0 | -1 | 2775.5823 | 3.205 | -51.4532 | 2.9335 | -51.0609 | 8.0942 | 2.9558 | 4.6866 | 3.2708
346 | B8 | IEEE 118 Bus Test Case | Tx 8-5 | 500 | 0 | 0 | -1 | 765.6708 | 0.88412 | 132.7212 | 0.78966 | 134.0326 | 2.2329 | 2.9558 | 4.6866 | 3.2708
347 | B8 | IEEE 118 Bus Test Case | Gen 8 | 500 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9558 | 4.6866 | 3.2708
348 | B8 | IEEE 118 Bus Test Case | Line 8-30 | 500 | 0 | 0 | -1 | 939.6673 | 1.085 | 127.9912 | 1.0373 | 128.3916 | 2.7403 | 2.9558 | 4.6866 | 3.2708
349 | B8 | IEEE 118 Bus Test Case | Line 8-9 | 500 | 0 | 0 | -1 | 1073.3326 | 1.2394 | 126.0573 | 1.1113 | 125.8341 | 3.1301 | 2.9558 | 4.6866 | 3.2708
350 | B49 | IEEE 118 Bus Test Case | Line 8-9 | 230 | 0 | 0 | -1 | 5218.6944 | 13.1001 | -52.0637 | 10.878 | -50.2988 | 31.939 | 11.0604 | 23.4712 | 13.3013
351 | B49 | IEEE 118 Bus Test Case | Line 47-49 | 230 | 0 | 0 | -1 | 350.892 | 0.88082 | 131.241 | 0.79068 | 131.8441 | 2.1475 | 11.0604 | 23.4712 | 13.3013
352 | B49 | IEEE 118 Bus Test Case | Line 49-69 | 230 | 0 | 0 | -1 | 258.6176 | 0.64919 | 136.2747 | 0.61953 | 136.4511 | 1.5828 | 11.0604 | 23.4712 | 13.3013
353 | B49 | IEEE 118 Bus Test Case | Line 49-66 C1 | 230 | 0 | 0 | -1 | 824.061 | 2.0686 | 130.8131 | 1.9381 | 131.0687 | 5.0433 | 11.0604 | 23.4712 | 13.3013
354 | B49 | IEEE 118 Bus Test Case | Load 49 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 11.0604 | 23.4712 | 13.3013
355 | B49 | IEEE 118 Bus Test Case | Line 45-49 | 230 | 0 | 0 | -1 | 146.0804 | 0.36669 | 128.9238 | 0.32352 | 129.4627 | 0.89403 | 11.0604 | 23.4712 | 13.3013
356 | B49 | IEEE 118 Bus Test Case | Line 49-66 C2 | 230 | 0 | 0 | -1 | 824.061 | 2.0686 | 130.8131 | 1.9381 | 131.0687 | 5.0433 | 11.0604 | 23.4712 | 13.3013
357 | B49 | IEEE 118 Bus Test Case | Line 42-49 C1 | 230 | 0 | 0 | -1 | 100.7573 | 0.25292 | 129.033 | 0.24458 | 129.3529 | 0.61665 | 11.0604 | 23.4712 | 13.3013
358 | B49 | IEEE 118 Bus Test Case | Line 42-49 C2 | 230 | 0 | 0 | -1 | 100.7573 | 0.25292 | 129.033 | 0.24458 | 129.3529 | 0.61665 | 11.0604 | 23.4712 | 13.3013
359 | B49 | IEEE 118 Bus Test Case | Line 49-54 C1 | 230 | 0 | 0 | -1 | 165.7195 | 0.41599 | 120.5599 | 0.36869 | 121.2356 | 1.0142 | 11.0604 | 23.4712 | 13.3013
360 | B49 | IEEE 118 Bus Test Case | Line 48-49 | 230 | 0 | 0 | -1 | 158.0849 | 0.39683 | 128.5875 | 0.33375 | 129.0803 | 0.9675 | 11.0604 | 23.4712 | 13.3013
361 | B49 | IEEE 118 Bus Test Case | Line 49-50 | 230 | 0 | 0 | -1 | 150.2025 | 0.37704 | 124.9885 | 0.33626 | 125.6865 | 0.91926 | 11.0604 | 23.4712 | 13.3013
362 | B49 | IEEE 118 Bus Test Case | Line 49-54 C2 | 230 | 0 | 0 | -1 | 162.6523 | 0.40829 | 123.0108 | 0.36187 | 123.6864 | 0.99545 | 11.0604 | 23.4712 | 13.3013
363 | B49 | IEEE 118 Bus Test Case | Line 49-51 | 230 | 0 | 0 | -1 | 182.2411 | 0.45746 | 123.1895 | 0.40714 | 123.8894 | 1.1153 | 11.0604 | 23.4712 | 13.3013
364 | B49 | IEEE 118 Bus Test Case | Tx 49-125 | 230 | 0 | 0 | -1 | 1805.1008 | 4.5312 | 125.0601 | 2.9862 | 129.1258 | 11.0474 | 11.0604 | 23.4712 | 13.3013
365 | B87 | IEEE 118 Bus Test Case | Tx 49-125 | 230 | 0 | 0 | -1 | 830.7611 | 2.0854 | -41.2513 | 1.6448 | -40.6718 | 5.3741 | 1.681 | 3.5208 | 1.9668
366 | B87 | IEEE 118 Bus Test Case | Line 86-87 | 230 | 0 | 0 | -1 | 236.9586 | 0.59482 | 139.5702 | 0.59067 | 139.5604 | 1.5329 | 1.681 | 3.5208 | 1.9668
367 | B87 | IEEE 118 Bus Test Case | Tx 87-133 | 230 | 0 | 0 | -1 | 593.8365 | 1.4907 | 138.4209 | 1.0542 | 139.1981 | 3.8415 | 1.681 | 3.5208 | 1.9668
368 | B2 | IEEE 118 Bus Test Case | Tx 87-133 | 230 | 0 | 0 | -1 | 1145.4881 | 2.8754 | -44.6756 | 2.7284 | -44.5023 | 6.3293 | 2.7405 | 3.8958 | 2.8998
369 | B2 | IEEE 118 Bus Test Case | Line 1-2 | 230 | 0 | 0 | -1 | 280.8835 | 0.70508 | 134.8949 | 0.67391 | 134.9652 | 1.552 | 2.7405 | 3.8958 | 2.8998
370 | B2 | IEEE 118 Bus Test Case | Line 2-12 | 230 | 0 | 0 | -1 | 864.615 | 2.1704 | 135.464 | 2.0545 | 135.6723 | 4.7774 | 2.7405 | 3.8958 | 2.8998
371 | B2 | IEEE 118 Bus Test Case | Load 2 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7405 | 3.8958 | 2.8998
372 | B70 | IEEE 118 Bus Test Case | Load 2 | 230 | 0 | 0 | -1 | 1567.1226 | 3.9338 | -46.6491 | 3.841 | -46.5936 | 8.5321 | 3.8486 | 5.5299 | 3.965
373 | B70 | IEEE 118 Bus Test Case | Gen 70 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8486 | 5.5299 | 3.965
374 | B70 | IEEE 118 Bus Test Case | Load 70 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8486 | 5.5299 | 3.965
375 | B70 | IEEE 118 Bus Test Case | Line 70-71 | 230 | 0 | 0 | -1 | 150.4921 | 0.37777 | 142.1544 | 0.37086 | 142.3142 | 0.81934 | 3.8486 | 5.5299 | 3.965
376 | B70 | IEEE 118 Bus Test Case | Line 70-74 | 230 | 0 | 0 | -1 | 259.803 | 0.65216 | 132.9168 | 0.63696 | 132.9707 | 1.4145 | 3.8486 | 5.5299 | 3.965
377 | B70 | IEEE 118 Bus Test Case | Line 69-70 | 230 | 0 | 0 | -1 | 678.6532 | 1.7036 | 132.367 | 1.6589 | 132.3695 | 3.6949 | 3.8486 | 5.5299 | 3.965
378 | B70 | IEEE 118 Bus Test Case | Line 70-75 | 230 | 0 | 0 | -1 | 324.7796 | 0.81527 | 134.0454 | 0.79626 | 134.0993 | 1.7682 | 3.8486 | 5.5299 | 3.965
379 | B70 | IEEE 118 Bus Test Case | Line 24-70 | 230 | 0 | 0 | -1 | 155.8716 | 0.39127 | 128.4386 | 0.38412 | 128.5984 | 0.84863 | 3.8486 | 5.5299 | 3.965
380 | B22 | IEEE 118 Bus Test Case | Line 24-70 | 230 | 0 | 0 | -1 | 691.2519 | 1.7352 | -45.8345 | 1.7006 | -45.7632 | 3.8275 | 1.7035 | 2.4155 | 1.7501
381 | B22 | IEEE 118 Bus Test Case | Load 22 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7035 | 2.4155 | 1.7501
382 | B22 | IEEE 118 Bus Test Case | Line 22-23 | 230 | 0 | 0 | -1 | 442.6621 | 1.1112 | 137.0359 | 1.0863 | 137.1302 | 2.451 | 1.7035 | 2.4155 | 1.7501
383 | B22 | IEEE 118 Bus Test Case | Line 21-22 | 230 | 0 | 0 | -1 | 250.1293 | 0.62788 | 129.0811 | 0.61815 | 129.1475 | 1.385 | 1.7035 | 2.4155 | 1.7501
384 | B107 | IEEE 118 Bus Test Case | Line 21-22 | 230 | 0 | 0 | -1 | 582.6338 | 1.4625 | -35.895 | 1.4066 | -35.8628 | 3.0532 | 1.4112 | 1.9971 | 1.4724
385 | B107 | IEEE 118 Bus Test Case | Gen 107 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4112 | 1.9971 | 1.4724
386 | B107 | IEEE 118 Bus Test Case | Load 107 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4112 | 1.9971 | 1.4724
387 | B107 | IEEE 118 Bus Test Case | Line 105-107 | 230 | 0 | 0 | -1 | 309.105 | 0.77592 | 144.5626 | 0.74549 | 144.5909 | 1.6198 | 1.4112 | 1.9971 | 1.4724
388 | B107 | IEEE 118 Bus Test Case | Line 106-107 | 230 | 0 | 0 | -1 | 273.5498 | 0.68667 | 143.5879 | 0.66118 | 143.6256 | 1.4335 | 1.4112 | 1.9971 | 1.4724
389 | B107 | IEEE 118 Bus Test Case | Shunt 107 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4112 | 1.9971 | 1.4724
390 | B1 | IEEE 118 Bus Test Case | Shunt 107 | 230 | 0 | 0 | -1 | 989.4084 | 2.4836 | -45.5496 | 2.383 | -45.4619 | 5.441 | 2.3912 | 3.3922 | 2.5043
391 | B1 | IEEE 118 Bus Test Case | Gen 1 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3912 | 3.3922 | 2.5043
392 | B1 | IEEE 118 Bus Test Case | Line 1-3 | 230 | 0 | 0 | -1 | 606.7306 | 1.523 | 133.7612 | 1.4651 | 133.8138 | 3.3366 | 2.3912 | 3.3922 | 2.5043
393 | B1 | IEEE 118 Bus Test Case | Line 1-2 | 230 | 0 | 0 | -1 | 382.7913 | 0.96089 | 135.5429 | 0.9182 | 135.6938 | 2.1051 | 2.3912 | 3.3922 | 2.5043
394 | B1 | IEEE 118 Bus Test Case | Load 1 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3912 | 3.3922 | 2.5043
395 | B105 | IEEE 118 Bus Test Case | Load 1 | 230 | 0 | 0 | -1 | 1398.3634 | 3.5102 | -35.9105 | 3.1933 | -35.8561 | 7.6383 | 3.2193 | 4.5756 | 3.5385
396 | B105 | IEEE 118 Bus Test Case | Gen 105 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2193 | 4.5756 | 3.5385
397 | B105 | IEEE 118 Bus Test Case | Shunt 105 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2193 | 4.5756 | 3.5385
398 | B105 | IEEE 118 Bus Test Case | Line 105-108 | 230 | 0 | 0 | -1 | 266.398 | 0.66872 | 149.5502 | 0.58828 | 149.359 | 1.4551 | 3.2193 | 4.5756 | 3.5385
399 | B105 | IEEE 118 Bus Test Case | Line 104-105 | 230 | 0 | 0 | -1 | 512.9094 | 1.2875 | 141.5224 | 1.1816 | 141.6842 | 2.8017 | 3.2193 | 4.5756 | 3.5385
400 | B105 | IEEE 118 Bus Test Case | Line 105-107 | 230 | 0 | 0 | -1 | 34.3734 | 0.086285 | 143.7049 | 0.08041 | 143.86 | 0.18776 | 3.2193 | 4.5756 | 3.5385
401 | B105 | IEEE 118 Bus Test Case | Line 103-105 | 230 | 0 | 0 | -1 | 353.2377 | 0.8867 | 145.3343 | 0.80105 | 145.5497 | 1.9295 | 3.2193 | 4.5756 | 3.5385
402 | B105 | IEEE 118 Bus Test Case | Line 105-106 | 230 | 0 | 0 | -1 | 233.4593 | 0.58603 | 141.6787 | 0.54613 | 141.8338 | 1.2752 | 3.2193 | 4.5756 | 3.5385
403 | B105 | IEEE 118 Bus Test Case | Load 105 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2193 | 4.5756 | 3.5385
404 | B34 | IEEE 118 Bus Test Case | Load 105 | 230 | 0 | 0 | -1 | 1915.9116 | 4.8094 | -50.6051 | 4.6649 | -50.3206 | 11.2846 | 4.6767 | 6.8978 | 4.8667
405 | B34 | IEEE 118 Bus Test Case | Gen 34 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6767 | 6.8978 | 4.8667
406 | B34 | IEEE 118 Bus Test Case | Load 34 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6767 | 6.8978 | 4.8667
407 | B34 | IEEE 118 Bus Test Case | Line 19-34 | 230 | 0 | 0 | -1 | 212.0374 | 0.53226 | 136.7905 | 0.51309 | 137.1999 | 1.2489 | 4.6767 | 6.8978 | 4.8667
408 | B34 | IEEE 118 Bus Test Case | Line 34-43 | 230 | 0 | 0 | -1 | 142.9554 | 0.35885 | 127.2589 | 0.34839 | 127.4962 | 0.842 | 4.6767 | 6.8978 | 4.8667
409 | B34 | IEEE 118 Bus Test Case | Line 34-36 | 230 | 0 | 0 | -1 | 152.3867 | 0.38252 | 128.1232 | 0.37132 | 128.4024 | 0.89755 | 4.6767 | 6.8978 | 4.8667
410 | B34 | IEEE 118 Bus Test Case | Line 34-37 | 230 | 0 | 0 | -1 | 1410.5552 | 3.5408 | 128.64 | 3.4371 | 128.9192 | 8.3081 | 4.6767 | 6.8978 | 4.8667
411 | B34 | IEEE 118 Bus Test Case | Shunt 34 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6767 | 6.8978 | 4.8667
412 | B43 | IEEE 118 Bus Test Case | Shunt 34 | 230 | 0 | 0 | -1 | 639.2216 | 1.6046 | -48.8665 | 1.5859 | -48.746 | 3.4443 | 1.5874 | 2.248 | 1.6167
413 | B43 | IEEE 118 Bus Test Case | Load 43 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5874 | 2.248 | 1.6167
414 | B43 | IEEE 118 Bus Test Case | Line 34-43 | 230 | 0 | 0 | -1 | 430.3359 | 1.0802 | 132.0481 | 1.0701 | 132.1399 | 2.3188 | 1.5874 | 2.248 | 1.6167
415 | B43 | IEEE 118 Bus Test Case | Line 43-44 | 230 | 0 | 0 | -1 | 209.0535 | 0.52477 | 129.2506 | 0.51615 | 129.417 | 1.1264 | 1.5874 | 2.248 | 1.6167
416 | B41 | IEEE 118 Bus Test Case | Line 43-44 | 230 | 0 | 0 | -1 | 831.0732 | 2.0862 | -47.1742 | 2.0567 | -47.023 | 4.3878 | 2.0591 | 2.9142 | 2.1006
417 | B41 | IEEE 118 Bus Test Case | Line 41-42 | 230 | 0 | 0 | -1 | 275.2802 | 0.69101 | 131.0538 | 0.67933 | 131.2347 | 1.4534 | 2.0591 | 2.9142 | 2.1006
418 | B41 | IEEE 118 Bus Test Case | Load 41 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0591 | 2.9142 | 2.1006
419 | B41 | IEEE 118 Bus Test Case | Line 40-41 | 230 | 0 | 0 | -1 | 555.9898 | 1.3957 | 133.703 | 1.3778 | 133.8359 | 2.9355 | 2.0591 | 2.9142 | 2.1006
420 | B52 | IEEE 118 Bus Test Case | Line 40-41 | 230 | 0 | 0 | -1 | 836.4911 | 2.0998 | -49.5101 | 2.0344 | -49.0901 | 4.3138 | 2.0397 | 2.8873 | 2.113
421 | B52 | IEEE 118 Bus Test Case | Line 51-52 | 230 | 0 | 0 | -1 | 586.638 | 1.4726 | 133.5811 | 1.4299 | 133.9574 | 3.0253 | 2.0397 | 2.8873 | 2.113
422 | B52 | IEEE 118 Bus Test Case | Load 52 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0397 | 2.8873 | 2.113
423 | B52 | IEEE 118 Bus Test Case | Line 52-53 | 230 | 0 | 0 | -1 | 252.6945 | 0.63432 | 123.2983 | 0.61126 | 123.7662 | 1.3031 | 2.0397 | 2.8873 | 2.113
424 | B60 | IEEE 118 Bus Test Case | Line 52-53 | 230 | 0 | 0 | -1 | 2836.4016 | 7.12 | -53.3579 | 6.543 | -52.6086 | 17.4591 | 6.5903 | 10.5271 | 7.2342
425 | B60 | IEEE 118 Bus Test Case | Line 59-60 | 230 | 0 | 0 | -1 | 390.9598 | 0.98139 | 126.966 | 0.91112 | 127.799 | 2.4065 | 6.5903 | 10.5271 | 7.2342
426 | B60 | IEEE 118 Bus Test Case | Line 60-61 | 230 | 0 | 0 | -1 | 1951.7561 | 4.8993 | 125.8895 | 4.4717 | 126.6377 | 12.0138 | 6.5903 | 10.5271 | 7.2342
427 | B60 | IEEE 118 Bus Test Case | Line 60-62 | 230 | 0 | 0 | -1 | 494.4154 | 1.2411 | 129.3576 | 1.1618 | 129.9737 | 3.0433 | 6.5903 | 10.5271 | 7.2342
428 | B60 | IEEE 118 Bus Test Case | Load 60 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5903 | 10.5271 | 7.2342
429 | B92 | IEEE 118 Bus Test Case | Load 60 | 230 | 0 | 0 | -1 | 2582.9319 | 6.4837 | -38.0788 | 5.9687 | -38.0086 | 15.0227 | 6.011 | 8.732 | 6.5556
430 | B92 | IEEE 118 Bus Test Case | Gen 92 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 6.011 | 8.732 | 6.5556
431 | B92 | IEEE 118 Bus Test Case | Line 89-92 C2 | 230 | 0 | 0 | -1 | 306.982 | 0.77059 | 145.3416 | 0.70261 | 145.624 | 1.7855 | 6.011 | 8.732 | 6.5556
432 | B92 | IEEE 118 Bus Test Case | Line 92-94 | 230 | 0 | 0 | -1 | 322.1569 | 0.80868 | 139.9347 | 0.76059 | 139.6868 | 1.8737 | 6.011 | 8.732 | 6.5556
433 | B92 | IEEE 118 Bus Test Case | Load 92 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 6.011 | 8.732 | 6.5556
434 | B92 | IEEE 118 Bus Test Case | Line 92-93 | 230 | 0 | 0 | -1 | 321.0185 | 0.80583 | 139.6916 | 0.7579 | 139.4438 | 1.8671 | 6.011 | 8.732 | 6.5556
435 | B92 | IEEE 118 Bus Test Case | Line 89-92 C1 | 230 | 0 | 0 | -1 | 971.8158 | 2.4395 | 142.4737 | 2.2243 | 142.7561 | 5.6522 | 6.011 | 8.732 | 6.5556
436 | B92 | IEEE 118 Bus Test Case | Line 92-102 | 230 | 0 | 0 | -1 | 245.3586 | 0.6159 | 138.9566 | 0.56725 | 138.9443 | 1.427 | 6.011 | 8.732 | 6.5556
437 | B92 | IEEE 118 Bus Test Case | Line 91-92 | 230 | 0 | 0 | -1 | 170.1551 | 0.42713 | 147.8111 | 0.38944 | 148.0935 | 0.98965 | 6.011 | 8.732 | 6.5556
438 | B92 | IEEE 118 Bus Test Case | Line 92-100 | 230 | 0 | 0 | -1 | 247.8567 | 0.62217 | 139.886 | 0.57303 | 139.8737 | 1.4416 | 6.011 | 8.732 | 6.5556
439 | B73 | IEEE 118 Bus Test Case | Line 92-100 | 230 | 0 | 0 | -1 | 720.2839 | 1.8081 | -47.7811 | 1.7884 | -47.74 | 3.9157 | 1.79 | 2.5395 | 1.8223
440 | B73 | IEEE 118 Bus Test Case | Gen 73 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 1.79 | 2.5395 | 1.8223
441 | B73 | IEEE 118 Bus Test Case | Line 71-73 | 230 | 0 | 0 | -1 | 720.2839 | 1.8081 | 132.2189 | 1.7884 | 132.26 | 3.9157 | 1.79 | 2.5395 | 1.8223
442 | B119 | IEEE 118 Bus Test Case | Line 71-73 | 22 | 0 | 0 | -1 | 3631.5732 | 95.3041 | -55.0336 | 76.9414 | -54.8651 | 255.9121 | 78.4487 | 168.3613 | 99.6674
443 | B119 | IEEE 118 Bus Test Case | Gen 10 | 22 | 0 | 0 | -1 | 2809.8629 | 73.7398 | -55.9246 | 56.1932 | -56.0875 | 198.0073 | 78.4487 | 168.3613 | 99.6674
444 | B119 | IEEE 118 Bus Test Case | Tx 10-119 | 22 | 0 | 0 | -1 | 823.2105 | 21.6037 | 128.009 | 20.7956 | 128.4396 | 58.0105 | 78.4487 | 168.3613 | 99.6674
445 | B131 | IEEE 118 Bus Test Case | Tx 10-119 | 22 | 0 | 0 | -1 | 7263.502 | 190.6175 | -54.2149 | 164.4505 | -53.4927 | 495.0842 | 166.5985 | 338.0835 | 195.8848
446 | B131 | IEEE 118 Bus Test Case | Gen 69 | 22 | 0 | 0 | -1 | 2776.494 | 72.8641 | -58.1011 | 55.4839 | -58.1851 | 189.2473 | 166.5985 | 338.0835 | 195.8848
447 | B131 | IEEE 118 Bus Test Case | Tx 69-131 | 22 | 0 | 0 | -1 | 4497.3307 | 118.0243 | 128.1831 | 109.247 | 128.8885 | 306.5405 | 166.5985 | 338.0835 | 195.8848
448 | B123 | IEEE 118 Bus Test Case | Tx 69-131 | 13.8 | 0 | 0 | -1 | 1632.7268 | 68.3084 | -42.0994 | 60.1508 | -40.9692 | 160.2666 | 60.8204 | 108.7673 | 69.1226
449 | B123 | IEEE 118 Bus Test Case | Tx 31-123 | 13.8 | 0 | 0 | -1 | 1067.7018 | 44.6694 | 135.3995 | 43.3295 | 135.2639 | 104.8044 | 60.8204 | 108.7673 | 69.1226
450 | B123 | IEEE 118 Bus Test Case | Gen 31 | 13.8 | 0 | 0 | -1 | 567.9566 | 23.7616 | -37.3937 | 17.1527 | -31.4164 | 55.75 | 60.8204 | 108.7673 | 69.1226
451 | B124 | IEEE 118 Bus Test Case | Gen 31 | 13.8 | 0 | 0 | -1 | 1673.7143 | 70.0231 | -50.793 | 61.3679 | -49.5341 | 160.5548 | 62.0783 | 112.8445 | 70.755
452 | B124 | IEEE 118 Bus Test Case | Gen 46 | 13.8 | 0 | 0 | -1 | 607.0831 | 25.3985 | -57.3885 | 18.2107 | -55.9308 | 58.2358 | 62.0783 | 112.8445 | 70.755
453 | B124 | IEEE 118 Bus Test Case | Tx 46-124 | 13.8 | 0 | 0 | -1 | 1072.9174 | 44.8876 | 132.9333 | 43.3181 | 133.1505 | 102.922 | 62.0783 | 112.8445 | 70.755
454 | B133 | IEEE 118 Bus Test Case | Tx 46-124 | 13.8 | 0 | 0 | -1 | 830.7611 | 34.7565 | -41.2513 | 27.4138 | -40.6718 | 89.5687 | 28.0166 | 58.6794 | 32.7806
455 | B133 | IEEE 118 Bus Test Case | Tx 87-133 | 13.8 | 0 | 0 | -1 | 236.9586 | 9.9136 | 139.5702 | 9.8444 | 139.5604 | 25.5478 | 28.0166 | 58.6794 | 32.7806
456 | B133 | IEEE 118 Bus Test Case | Gen 87 | 13.8 | 0 | 0 | -1 | 593.8365 | 24.8443 | -41.5791 | 17.5695 | -40.8019 | 64.0247 | 28.0166 | 58.6794 | 32.7806
457 | B125 | IEEE 118 Bus Test Case | Gen 87 | 20 | 0 | 0 | -1 | 5218.6944 | 150.6507 | -52.0637 | 125.0967 | -50.2988 | 367.2983 | 127.1943 | 269.9191 | 152.9651
458 | B125 | IEEE 118 Bus Test Case | Tx 49-125 | 20 | 0 | 0 | -1 | 3417.0681 | 98.6423 | 129.4552 | 90.7581 | 129.9189 | 240.4976 | 127.1943 | 269.9191 | 152.9651
459 | B125 | IEEE 118 Bus Test Case | Gen 49 | 20 | 0 | 0 | -1 | 1805.1008 | 52.1088 | -54.9399 | 34.3409 | -50.8742 | 127.0453 | 127.1943 | 269.9191 | 152.9651
460 | B127 | IEEE 118 Bus Test Case | Gen 49 | 20 | 0 | 0 | -1 | 3608.8864 | 104.1796 | -53.721 | 92.6148 | -52.3259 | 263.3561 | 93.5641 | 186.9808 | 106.3377
461 | B127 | IEEE 118 Bus Test Case | Gen 59 | 20 | 0 | 0 | -1 | 989.4934 | 28.5642 | -53.2146 | 22.5635 | -50.0841 | 72.2076 | 93.5641 | 186.9808 | 106.3377
462 | B127 | IEEE 118 Bus Test Case | Tx 59-127 | 20 | 0 | 0 | -1 | 2619.4463 | 75.6169 | 126.0877 | 70.0742 | 126.9524 | 191.1524 | 93.5641 | 186.9808 | 106.3377
463 | B128 | IEEE 118 Bus Test Case | Tx 59-127 | 20 | 0 | 0 | -1 | 3627.9856 | 104.7309 | -55.0449 | 93.701 | -53.9995 | 270.3055 | 94.6064 | 202.4334 | 107.4187
464 | B128 | IEEE 118 Bus Test Case | Tx 61-128 | 20 | 0 | 0 | -1 | 2713.3197 | 78.3268 | 125.3486 | 73.4665 | 126.0998 | 202.1577 | 94.6064 | 202.4334 | 107.4187
465 | B128 | IEEE 118 Bus Test Case | Gen 61 | 20 | 0 | 0 | -1 | 914.9197 | 26.4115 | -56.2119 | 20.235 | -54.3602 | 68.1667 | 94.6064 | 202.4334 | 107.4187
466 | B129 | IEEE 118 Bus Test Case | Gen 61 | 24 | 0 | 0 | -1 | 10018.8168 | 241.0153 | -54.7647 | 201.3513 | -53.7078 | 642.7734 | 204.6071 | 425.0231 | 250.7571
467 | B129 | IEEE 118 Bus Test Case | Tx 65-129 | 24 | 0 | 0 | -1 | 7211.6933 | 173.4864 | 123.7353 | 149.6919 | 124.6682 | 462.6779 | 204.6071 | 425.0231 | 250.7571
468 | B129 | IEEE 118 Bus Test Case | Gen 65 | 24 | 0 | 0 | -1 | 2815.929 | 67.7407 | -50.9209 | 51.8933 | -49.0185 | 180.6605 | 204.6071 | 425.0231 | 250.7571
469 | B130 | IEEE 118 Bus Test Case | Gen 65 | 24 | 0 | 0 | -1 | 8418.56 | 202.5191 | -54.9156 | 168.8151 | -53.9401 | 538.7419 | 171.5817 | 371.2362 | 210.3628
470 | B130 | IEEE 118 Bus Test Case | Tx 66-130 | 24 | 0 | 0 | -1 | 5710.6135 | 137.376 | 124.7857 | 120.5566 | 125.7561 | 365.4481 | 171.5817 | 371.2362 | 210.3628
471 | B130 | IEEE 118 Bus Test Case | Gen 66 | 24 | 0 | 0 | -1 | 2708.1877 | 65.1489 | -54.2858 | 48.2645 | -53.1814 | 173.3092 | 171.5817 | 371.2362 | 210.3628
472 | B134 | IEEE 118 Bus Test Case | Gen 66 | 20 | 0 | 0 | -1 | 3693.2551 | 106.6151 | -40.9227 | 92.1409 | -40.3139 | 277.1656 | 93.329 | 235.2546 | 109.5948
473 | B134 | IEEE 118 Bus Test Case | Tx 89-134 | 20 | 0 | 0 | -1 | 1161.8808 | 33.5406 | 137.9362 | 31.8217 | 137.6897 | 87.195 | 93.329 | 235.2546 | 109.5948
474 | B134 | IEEE 118 Bus Test Case | Gen 89 | 20 | 0 | 0 | -1 | 2531.7105 | 73.0842 | -40.399 | 60.3487 | -39.2613 | 189.9958 | 93.329 | 235.2546 | 109.5948
475 | B132 | IEEE 118 Bus Test Case | Gen 89 | 22 | 0 | 0 | -1 | 6079.8779 | 159.5554 | -49.5318 | 137.5689 | -48.6827 | 406.9411 | 139.3737 | 283.1941 | 163.1602
476 | B132 | IEEE 118 Bus Test Case | Gen 80 | 22 | 0 | 0 | -1 | 3077.4988 | 80.7634 | -51.2174 | 63.4468 | -50.0257 | 205.9845 | 139.3737 | 283.1941 | 163.1602
477 | B132 | IEEE 118 Bus Test Case | Tx 80-132 | 22 | 0 | 0 | -1 | 3005.0744 | 78.8628 | 132.1943 | 74.1544 | 132.4665 | 201.137 | 139.3737 | 283.1941 | 163.1602
478 | B120 | IEEE 118 Bus Test Case | Tx 80-132 | 15.5 | 0 | 0 | -1 | 2450.9396 | 91.2936 | -47.9589 | 81.306 | -47.1666 | 225.5646 | 82.1258 | 141.8162 | 92.846
479 | B120 | IEEE 118 Bus Test Case | Tx 12-120 | 15.5 | 0 | 0 | -1 | 1451.4325 | 54.0635 | 131.0989 | 51.8985 | 131.1332 | 133.578 | 82.1258 | 141.8162 | 92.846
480 | B120 | IEEE 118 Bus Test Case | Gen 12 | 15.5 | 0 | 0 | -1 | 999.9883 | 37.248 | -46.5913 | 29.4705 | -44.1717 | 92.0308 | 82.1258 | 141.8162 | 92.846
481 | B126 | IEEE 118 Bus Test Case | Gen 12 | 13.8 | 0 | 0 | -1 | 2608.0878 | 109.1145 | -52.1642 | 95.819 | -50.3929 | 252.8952 | 96.9104 | 164.0907 | 110.3254
482 | B126 | IEEE 118 Bus Test Case | Gen 54 | 13.8 | 0 | 0 | -1 | 668.6301 | 27.9735 | -63.305 | 18.6084 | -61.5983 | 64.8342 | 96.9104 | 164.0907 | 110.3254
483 | B126 | IEEE 118 Bus Test Case | Tx 54-126 | 13.8 | 0 | 0 | -1 | 1956.3281 | 81.8468 | 131.6222 | 77.6497 | 132.2763 | 189.6969 | 96.9104 | 164.0907 | 110.3254
484 | B136 | IEEE 118 Bus Test Case | Tx 54-126 | 13.8 | 0 | 0 | -1 | 2385.695 | 99.8103 | -39.7412 | 82.9056 | -38.8347 | 235.5879 | 84.2932 | 147.6219 | 101.0443
485 | B136 | IEEE 118 Bus Test Case | Tx 103-136 | 13.8 | 0 | 0 | -1 | 1627.4014 | 68.0856 | 143.2384 | 61.0014 | 143.4732 | 160.7063 | 84.2932 | 147.6219 | 101.0443
486 | B136 | IEEE 118 Bus Test Case | Gen 103 | 13.8 | 0 | 0 | -1 | 765.1842 | 32.013 | -46.0884 | 22.0907 | -45.2195 | 75.5621 | 84.2932 | 147.6219 | 101.0443
487 | B137 | IEEE 118 Bus Test Case | Gen 103 | 13.8 | 0 | 0 | -1 | 1120.1858 | 46.8652 | -39.5877 | 36.5845 | -38.6112 | 116.3123 | 37.4284 | 77.0017 | 43.6897
488 | B137 | IEEE 118 Bus Test Case | Tx 111-137 | 13.8 | 0 | 0 | -1 | 445.4213 | 18.6351 | 143.2527 | 17.958 | 143.1616 | 46.2495 | 37.4284 | 77.0017 | 43.6897
489 | B137 | IEEE 118 Bus Test Case | Gen 111 | 13.8 | 0 | 0 | -1 | 675.6723 | 28.2681 | -41.4597 | 18.6434 | -40.3187 | 70.1571 | 37.4284 | 77.0017 | 43.6897
490 | B121 | IEEE 118 Bus Test Case | Gen 111 | 20 | 0 | 0 | -1 | 4205.8053 | 121.4111 | -49.8684 | 96.4886 | -49.0516 | 327.9259 | 98.5344 | 268.3536 | 118.2068
491 | B121 | IEEE 118 Bus Test Case | Gen 25 | 20 | 0 | 0 | -1 | 1752.7731 | 50.5982 | -51.3101 | 32.1499 | -50.4163 | 136.6634 | 98.5344 | 268.3536 | 118.2068
492 | B121 | IEEE 118 Bus Test Case | Tx 25-121 | 20 | 0 | 0 | -1 | 2453.9834 | 70.8404 | 131.1613 | 64.3524 | 131.6301 | 191.3367 | 98.5344 | 268.3536 | 118.2068
493 | B135 | IEEE 118 Bus Test Case | Tx 25-121 | 20 | 0 | 0 | -1 | 4109.6496 | 118.6354 | -41.9073 | 94.76 | -40.4633 | 295.0819 | 96.7198 | 227.4024 | 111.333
494 | B135 | IEEE 118 Bus Test Case | Gen 100 | 20 | 0 | 0 | -1 | 1798.7592 | 51.9257 | -42.316 | 34.3058 | -38.1991 | 129.1549 | 96.7198 | 227.4024 | 111.333
495 | B135 | IEEE 118 Bus Test Case | Tx 100-135 | 20 | 0 | 0 | -1 | 2310.9718 | 66.712 | 138.4108 | 60.4962 | 138.2529 | 165.9328 | 96.7198 | 227.4024 | 111.333
496 | B122 | IEEE 118 Bus Test Case | Tx 100-135 | 24 | 0 | 0 | -1 | 4409.0697 | 106.0657 | -49.7397 | 87.2859 | -48.977 | 287.5195 | 88.8274 | 231.1296 | 112.0047
497 | B122 | IEEE 118 Bus Test Case | Gen 26 | 24 | 0 | 0 | -1 | 1888.2439 | 45.4241 | -45.9902 | 38.1976 | -44.9305 | 123.1341 | 88.8274 | 231.1296 | 112.0047
498 | B122 | IEEE 118 Bus Test Case | Tx 26-122 | 24 | 0 | 0 | -1 | 2527.8852 | 60.8115 | 127.4605 | 49.2572 | 127.8861 | 164.8457 | 88.8274 | 231.1296 | 112.0047
499 | B102 | IEEE 118 Bus Test Case | Tx 26-122 | 230 | 0 | 0 | -1 | 1316.0042 | 3.3035 | -37.5132 | 3.1606 | -37.4723 | 7.3826 | 3.1723 | 4.5107 | 3.3337
500 | B102 | IEEE 118 Bus Test Case | Line 101-102 | 230 | 0 | 0 | -1 | 343.2428 | 0.86161 | 140.3729 | 0.81903 | 140.4175 | 1.9255 | 3.1723 | 4.5107 | 3.3337
501 | B102 | IEEE 118 Bus Test Case | Line 92-102 | 230 | 0 | 0 | -1 | 973.0774 | 2.4426 | 143.2323 | 2.3423 | 143.2654 | 5.4588 | 3.1723 | 4.5107 | 3.3337
502 | B102 | IEEE 118 Bus Test Case | Load 102 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1723 | 4.5107 | 3.3337
503 | B17 | IEEE 118 Bus Test Case | Load 102 | 230 | 0 | 0 | -1 | 2874.7319 | 7.2162 | -48.1888 | 6.7177 | -47.7497 | 17.6637 | 6.7586 | 10.7507 | 7.3304
504 | B17 | IEEE 118 Bus Test Case | Line 16-17 | 230 | 0 | 0 | -1 | 194.0832 | 0.48719 | 135.2461 | 0.44528 | 135.9857 | 1.1925 | 6.7586 | 10.7507 | 7.3304
505 | B17 | IEEE 118 Bus Test Case | Line 17-18 | 230 | 0 | 0 | -1 | 170.9073 | 0.42901 | 131.0663 | 0.40546 | 131.4166 | 1.0501 | 6.7586 | 10.7507 | 7.3304
506 | B17 | IEEE 118 Bus Test Case | Line 17-113 | 230 | 0 | 0 | -1 | 208.0654 | 0.52229 | 141.9406 | 0.47418 | 143.0511 | 1.2784 | 6.7586 | 10.7507 | 7.3304
507 | B17 | IEEE 118 Bus Test Case | Tx 30-17 | 230 | 0 | 0 | -1 | 1653.8354 | 4.1515 | 127.1126 | 3.9141 | 127.3979 | 10.1619 | 6.7586 | 10.7507 | 7.3304
508 | B17 | IEEE 118 Bus Test Case | Line 17-31 | 230 | 0 | 0 | -1 | 303.7872 | 0.76257 | 144.3812 | 0.67278 | 146.4204 | 1.8666 | 6.7586 | 10.7507 | 7.3304
509 | B17 | IEEE 118 Bus Test Case | Load 17 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7586 | 10.7507 | 7.3304
510 | B17 | IEEE 118 Bus Test Case | Line 15-17 | 230 | 0 | 0 | -1 | 361.2552 | 0.90683 | 135.5187 | 0.85151 | 135.9154 | 2.2197 | 6.7586 | 10.7507 | 7.3304
511 | B30 | IEEE 118 Bus Test Case | Line 15-17 | 500 | 0 | 0 | -1 | 3289.5086 | 3.7984 | -49.2938 | 3.5252 | -48.8202 | 9.413 | 3.5476 | 5.4427 | 3.8646
512 | B30 | IEEE 118 Bus Test Case | Line 30-38 | 500 | 0 | 0 | -1 | 663.8257 | 0.76652 | 124.0413 | 0.74711 | 124.1565 | 1.8995 | 3.5476 | 5.4427 | 3.8646
513 | B30 | IEEE 118 Bus Test Case | Tx 30-17 | 500 | 0 | 0 | -1 | 961.3175 | 1.11 | 134.7353 | 1.0112 | 135.7052 | 2.7508 | 3.5476 | 5.4427 | 3.8646
514 | B30 | IEEE 118 Bus Test Case | Line 26-30 | 500 | 0 | 0 | -1 | 841.061 | 0.97117 | 134.1373 | 0.89382 | 134.8524 | 2.4067 | 3.5476 | 5.4427 | 3.8646
515 | B30 | IEEE 118 Bus Test Case | Line 8-30 | 500 | 0 | 0 | -1 | 832.676 | 0.96149 | 127.8952 | 0.88489 | 128.2206 | 2.3827 | 3.5476 | 5.4427 | 3.8646
516 | B11 | IEEE 118 Bus Test Case | Line 8-30 | 230 | 0 | 0 | -1 | 2150.949 | 5.3994 | -47.0257 | 4.942 | -46.5875 | 12.8463 | 4.9795 | 7.364 | 5.4695
517 | B11 | IEEE 118 Bus Test Case | Line 4-11 | 230 | 0 | 0 | -1 | 394.1605 | 0.98943 | 131.352 | 0.93254 | 131.4227 | 2.3541 | 4.9795 | 7.364 | 5.4695
518 | B11 | IEEE 118 Bus Test Case | Line 11-13 | 230 | 0 | 0 | -1 | 168.5446 | 0.42308 | 133.5478 | 0.40688 | 133.7576 | 1.0066 | 4.9795 | 7.364 | 5.4695
519 | B11 | IEEE 118 Bus Test Case | Line 5-11 | 230 | 0 | 0 | -1 | 445.6547 | 1.1187 | 131.2483 | 1.0544 | 131.319 | 2.6616 | 4.9795 | 7.364 | 5.4695
520 | B11 | IEEE 118 Bus Test Case | Line 11-12 | 230 | 0 | 0 | -1 | 1143.1871 | 2.8696 | 134.1219 | 2.5504 | 134.9503 | 6.8275 | 4.9795 | 7.364 | 5.4695
521 | B11 | IEEE 118 Bus Test Case | Load 11 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9795 | 7.364 | 5.4695
522 | B69 | IEEE 118 Bus Test Case | Load 11 | 230 | 0 | 0 | -1 | 7263.502 | 18.233 | -54.2149 | 15.7301 | -53.4927 | 47.3559 | 15.9355 | 32.3384 | 18.7368
523 | B69 | IEEE 118 Bus Test Case | Line 47-69 | 230 | 0 | 0 | -1 | 239.6935 | 0.60168 | 131.9565 | 0.55225 | 132.4337 | 1.5627 | 15.9355 | 32.3384 | 18.7368
524 | B69 | IEEE 118 Bus Test Case | Line 49-69 | 230 | 0 | 0 | -1 | 235.2535 | 0.59054 | 133.0736 | 0.54083 | 133.6423 | 1.5338 | 15.9355 | 32.3384 | 18.7368
525 | B69 | IEEE 118 Bus Test Case | Line 69-70 | 230 | 0 | 0 | -1 | 203.0596 | 0.50972 | 133.2986 | 0.48913 | 133.8306 | 1.3239 | 15.9355 | 32.3384 | 18.7368
526 | B69 | IEEE 118 Bus Test Case | Line 69-75 | 230 | 0 | 0 | -1 | 203.0868 | 0.50979 | 136.5017 | 0.48249 | 137.1945 | 1.3241 | 15.9355 | 32.3384 | 18.7368
527 | B69 | IEEE 118 Bus Test Case | Line 69-77 | 230 | 0 | 0 | -1 | 504.8803 | 1.2674 | 140.1888 | 1.1876 | 141.023 | 3.2917 | 15.9355 | 32.3384 | 18.7368
528 | B69 | IEEE 118 Bus Test Case | Tx 68-69 | 230 | 0 | 0 | -1 | 3132.3888 | 7.863 | 124.7361 | 7.2471 | 125.4041 | 20.4222 | 15.9355 | 32.3384 | 18.7368
529 | B69 | IEEE 118 Bus Test Case | Tx 69-131 | 230 | 0 | 0 | -1 | 2776.494 | 6.9696 | 121.8989 | 5.3072 | 121.8149 | 18.1019 | 15.9355 | 32.3384 | 18.7368
530 | B68 | IEEE 118 Bus Test Case | Tx 69-131 | 500 | 0 | 0 | -1 | 7758.3037 | 8.9585 | -54.6536 | 7.8938 | -53.8359 | 23.5008 | 7.9812 | 15.627 | 9.2399
531 | B68 | IEEE 118 Bus Test Case | Tx 68-69 | 500 | 0 | 0 | -1 | 3187.3345 | 3.6804 | 124.365 | 3.1154 | 125.2365 | 9.6548 | 7.9812 | 15.627 | 9.2399
532 | B68 | IEEE 118 Bus Test Case | Line 65-68 | 500 | 0 | 0 | -1 | 3383.3488 | 3.9068 | 125.7117 | 3.5123 | 126.3502 | 10.2486 | 7.9812 | 15.627 | 9.2399
533 | B68 | IEEE 118 Bus Test Case | Line 68-116 | 500 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9812 | 15.627 | 9.2399
534 | B68 | IEEE 118 Bus Test Case | Line 68-81 | 500 | 0 | 0 | -1 | 1188.6157 | 1.3725 | 126.9386 | 1.2671 | 127.9294 | 3.6005 | 7.9812 | 15.627 | 9.2399
535 | B83 | IEEE 118 Bus Test Case | Line 68-81 | 230 | 0 | 0 | -1 | 1497.6431 | 3.7594 | -38.198 | 3.6461 | -38.2555 | 7.8433 | 3.6554 | 5.1723 | 3.7846
536 | B83 | IEEE 118 Bus Test Case | Line 82-83 | 230 | 0 | 0 | -1 | 980.4019 | 2.461 | 138.0002 | 2.3992 | 137.909 | 5.1344 | 3.6554 | 5.1723 | 3.7846
537 | B83 | IEEE 118 Bus Test Case | Line 83-85 | 230 | 0 | 0 | -1 | 307.5123 | 0.77192 | 145.2598 | 0.74165 | 145.3718 | 1.6105 | 3.6554 | 5.1723 | 3.7846
538 | B83 | IEEE 118 Bus Test Case | Load 83 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6554 | 5.1723 | 3.7846
539 | B83 | IEEE 118 Bus Test Case | Shunt 83 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6554 | 5.1723 | 3.7846
540 | B83 | IEEE 118 Bus Test Case | Line 83-84 | 230 | 0 | 0 | -1 | 217.4669 | 0.54589 | 154.1377 | 0.52448 | 154.2497 | 1.1389 | 3.6554 | 5.1723 | 3.7846
541 | B36 | IEEE 118 Bus Test Case | Line 83-84 | 230 | 0 | 0 | -1 | 1474.3732 | 3.701 | -50.0091 | 3.6151 | -49.8174 | 8.4191 | 3.6222 | 5.2094 | 3.7381
542 | B36 | IEEE 118 Bus Test Case | Gen 36 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6222 | 5.2094 | 3.7381
543 | B36 | IEEE 118 Bus Test Case | Line 34-36 | 230 | 0 | 0 | -1 | 935.1061 | 2.3473 | 131.9231 | 2.2926 | 132.1157 | 5.3397 | 3.6222 | 5.2094 | 3.7381
544 | B36 | IEEE 118 Bus Test Case | Load 36 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6222 | 5.2094 | 3.7381
545 | B36 | IEEE 118 Bus Test Case | Line 35-36 | 230 | 0 | 0 | -1 | 540.7188 | 1.3573 | 126.6482 | 1.326 | 126.8391 | 3.0877 | 3.6222 | 5.2094 | 3.7381
546 | B75 | IEEE 118 Bus Test Case | Line 35-36 | 230 | 0 | 0 | -1 | 1827.6798 | 4.5879 | -43.8763 | 4.4599 | -43.8325 | 9.5756 | 4.4704 | 6.3285 | 4.6187
547 | B75 | IEEE 118 Bus Test Case | Line 69-75 | 230 | 0 | 0 | -1 | 672.1735 | 1.6873 | 137.0998 | 1.6353 | 137.0756 | 3.5216 | 4.4704 | 6.3285 | 4.6187
548 | B75 | IEEE 118 Bus Test Case | Load 75 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4704 | 6.3285 | 4.6187
549 | B75 | IEEE 118 Bus Test Case | Line 74-75 | 230 | 0 | 0 | -1 | 226.1332 | 0.56764 | 133.7947 | 0.55338 | 133.826 | 1.1848 | 4.4704 | 6.3285 | 4.6187
550 | B75 | IEEE 118 Bus Test Case | Line 75-77 | 230 | 0 | 0 | -1 | 367.5861 | 0.92272 | 137.6979 | 0.89774 | 137.8285 | 1.9259 | 4.4704 | 6.3285 | 4.6187
551 | B75 | IEEE 118 Bus Test Case | Line 70-75 | 230 | 0 | 0 | -1 | 282.6889 | 0.70961 | 134.9234 | 0.69178 | 134.9546 | 1.4811 | 4.4704 | 6.3285 | 4.6187
552 | B75 | IEEE 118 Bus Test Case | Line 75-118 | 230 | 0 | 0 | -1 | 279.6573 | 0.702 | 134.8046 | 0.68299 | 134.9352 | 1.4652 | 4.4704 | 6.3285 | 4.6187
553 | B67 | IEEE 118 Bus Test Case | Line 75-118 | 230 | 0 | 0 | -1 | 1448.9598 | 3.6372 | -49.356 | 3.5204 | -49.2408 | 8.091 | 3.53 | 5.0083 | 3.6697
554 | B67 | IEEE 118 Bus Test Case | Load 67 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.53 | 5.0083 | 3.6697
555 | B67 | IEEE 118 Bus Test Case | Line 62-67 | 230 | 0 | 0 | -1 | 567.6687 | 1.425 | 127.9021 | 1.3753 | 128.046 | 3.1699 | 3.53 | 5.0083 | 3.6697
556 | B67 | IEEE 118 Bus Test Case | Line 66-67 | 230 | 0 | 0 | -1 | 882.3589 | 2.2149 | 132.4076 | 2.1476 | 132.4963 | 4.9271 | 3.53 | 5.0083 | 3.6697
557 | B97 | IEEE 118 Bus Test Case | Line 66-67 | 230 | 0 | 0 | -1 | 1531.0592 | 3.8433 | -45.2098 | 3.7169 | -45.0717 | 8.6463 | 3.7273 | 5.3006 | 3.8796
558 | B97 | IEEE 118 Bus Test Case | Line 96-97 | 230 | 0 | 0 | -1 | 653.0663 | 1.6393 | 137.6999 | 1.5885 | 137.9051 | 3.6881 | 3.7273 | 5.3006 | 3.8796
559 | B97 | IEEE 118 Bus Test Case | Line 80-97 | 230 | 0 | 0 | -1 | 879.4599 | 2.2076 | 132.6299 | 2.1321 | 132.7109 | 4.9666 | 3.7273 | 5.3006 | 3.8796
560 | B97 | IEEE 118 Bus Test Case | Load 97 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7273 | 5.3006 | 3.8796
561 | B56 | IEEE 118 Bus Test Case | Load 97 | 230 | 0 | 0 | -1 | 2515.2667 | 6.3139 | -51.1796 | 5.6379 | -49.653 | 14.3395 | 5.6934 | 8.7619 | 6.3766
562 | B56 | IEEE 118 Bus Test Case | Gen 56 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6934 | 8.7619 | 6.3766
563 | B56 | IEEE 118 Bus Test Case | Line 55-56 | 230 | 0 | 0 | -1 | 351.8969 | 0.88334 | 126.0669 | 0.80426 | 127.2563 | 2.0062 | 5.6934 | 8.7619 | 6.3766
564 | B56 | IEEE 118 Bus Test Case | Line 56-58 | 230 | 0 | 0 | -1 | 210.1499 | 0.52752 | 135.6164 | 0.4961 | 136.4477 | 1.1981 | 5.6934 | 8.7619 | 6.3766
565 | B56 | IEEE 118 Bus Test Case | Load 56 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6934 | 8.7619 | 6.3766
566 | B56 | IEEE 118 Bus Test Case | Line 56-59 C1 | 230 | 0 | 0 | -1 | 242.0377 | 0.60757 | 132.829 | 0.57545 | 133.4805 | 1.3799 | 5.6934 | 8.7619 | 6.3766
567 | B56 | IEEE 118 Bus Test Case | Line 56-59 C2 | 230 | 0 | 0 | -1 | 253.6357 | 0.63668 | 133.2055 | 0.60302 | 133.8571 | 1.446 | 5.6934 | 8.7619 | 6.3766
568 | B56 | IEEE 118 Bus Test Case | Line 54-56 | 230 | 0 | 0 | -1 | 1220.1333 | 3.0628 | 125.2929 | 2.5912 | 127.1979 | 6.956 | 5.6934 | 8.7619 | 6.3766
569 | B56 | IEEE 118 Bus Test Case | Line 56-57 | 230 | 0 | 0 | -1 | 244.8864 | 0.61472 | 136.0448 | 0.58137 | 136.7278 | 1.3961 | 5.6934 | 8.7619 | 6.3766
570 | B94 | IEEE 118 Bus Test Case | Line 56-57 | 230 | 0 | 0 | -1 | 2535.1103 | 6.3637 | -37.8647 | 5.8931 | -37.8386 | 13.8345 | 5.9318 | 8.4158 | 6.4147
571 | B94 | IEEE 118 Bus Test Case | Line 92-94 | 230 | 0 | 0 | -1 | 329.0553 | 0.826 | 147.4334 | 0.77443 | 147.6734 | 1.7957 | 5.9318 | 8.4158 | 6.4147
572 | B94 | IEEE 118 Bus Test Case | Line 93-94 | 230 | 0 | 0 | -1 | 327.8926 | 0.82308 | 147.1904 | 0.77169 | 147.4304 | 1.7894 | 5.9318 | 8.4158 | 6.4147
573 | B94 | IEEE 118 Bus Test Case | Line 94-96 | 230 | 0 | 0 | -1 | 440.3035 | 1.1053 | 135.2531 | 1.0652 | 135.043 | 2.4028 | 5.9318 | 8.4158 | 6.4147
574 | B94 | IEEE 118 Bus Test Case | Line 94-95 | 230 | 0 | 0 | -1 | 385.8704 | 0.96862 | 134.7403 | 0.93349 | 134.5302 | 2.1058 | 5.9318 | 8.4158 | 6.4147
575 | B94 | IEEE 118 Bus Test Case | Line 94-100 | 230 | 0 | 0 | -1 | 1061.9286 | 2.6657 | 144.464 | 2.3743 | 144.8338 | 5.7951 | 5.9318 | 8.4158 | 6.4147
576 | B94 | IEEE 118 Bus Test Case | Load 94 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9318 | 8.4158 | 6.4147
577 | B25 | IEEE 118 Bus Test Case | Load 94 | 230 | 0 | 0 | -1 | 4205.8053 | 10.5575 | -49.8684 | 8.3903 | -49.0516 | 28.5153 | 8.5682 | 23.3351 | 10.2789
578 | B25 | IEEE 118 Bus Test Case | Line 23-25 | 230 | 0 | 0 | -1 | 366.1162 | 0.91903 | 130.63 | 0.88071 | 130.758 | 2.4823 | 8.5682 | 23.3351 | 10.2789
579 | B25 | IEEE 118 Bus Test Case | Line 25-27 | 230 | 0 | 0 | -1 | 213.4113 | 0.53571 | 134.9761 | 0.49732 | 135.5981 | 1.4469 | 8.5682 | 23.3351 | 10.2789
580 | B25 | IEEE 118 Bus Test Case | Tx 26-25 | 230 | 0 | 0 | -1 | 1874.9756 | 4.7066 | 130.8311 | 4.2192 | 131.3448 | 12.7123 | 8.5682 | 23.3351 | 10.2789
581 | B25 | IEEE 118 Bus Test Case | Tx 25-121 | 230 | 0 | 0 | -1 | 1752.7731 | 4.3998 | 128.6899 | 2.7956 | 129.5837 | 11.8838 | 8.5682 | 23.3351 | 10.2789
582 | B26 | IEEE 118 Bus Test Case | Tx 25-121 | 500 | 0 | 0 | -1 | 4409.0697 | 5.0912 | -49.7397 | 4.1897 | -48.977 | 13.8009 | 4.2637 | 11.0942 | 5.3762
583 | B26 | IEEE 118 Bus Test Case | Line 26-30 | 500 | 0 | 0 | -1 | 681.9894 | 0.78749 | 124.3816 | 0.75325 | 124.4099 | 2.1347 | 4.2637 | 11.0942 | 5.3762
584 | B26 | IEEE 118 Bus Test Case | Tx 26-25 | 500 | 0 | 0 | -1 | 1847.2434 | 2.133 | 128.5967 | 1.6131 | 129.5085 | 5.7821 | 4.2637 | 11.0942 | 5.3762
585 | B26 | IEEE 118 Bus Test Case | Tx 26-122 | 500 | 0 | 0 | -1 | 1888.2439 | 2.1804 | 134.0098 | 1.8335 | 135.0695 | 5.9104 | 4.2637 | 11.0942 | 5.3762
586 | B93 | IEEE 118 Bus Test Case | Tx 26-122 | 230 | 0 | 0 | -1 | 1427.983 | 3.5845 | -35.8563 | 3.4349 | -35.9222 | 7.5689 | 3.4472 | 4.8793 | 3.6098
587 | B93 | IEEE 118 Bus Test Case | Line 92-93 | 230 | 0 | 0 | -1 | 680.5782 | 1.7084 | 146.7488 | 1.6358 | 146.7617 | 3.6073 | 3.4472 | 4.8793 | 3.6098
588 | B93 | IEEE 118 Bus Test Case | Line 93-94 | 230 | 0 | 0 | -1 | 748.7474 | 1.8795 | 141.776 | 1.8026 | 141.6423 | 3.9687 | 3.4472 | 4.8793 | 3.6098
589 | B93 | IEEE 118 Bus Test Case | Load 93 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4472 | 4.8793 | 3.6098
590 | B59 | IEEE 118 Bus Test Case | Load 93 | 230 | 0 | 0 | -1 | 3608.8864 | 9.0591 | -53.721 | 8.0535 | -52.3259 | 22.9005 | 8.136 | 16.2592 | 9.2468
591 | B59 | IEEE 118 Bus Test Case | Line 54-59 | 230 | 0 | 0 | -1 | 208.0606 | 0.52228 | 122.2056 | 0.46738 | 123.4874 | 1.3203 | 8.136 | 16.2592 | 9.2468
592 | B59 | IEEE 118 Bus Test Case | Line 55-59 | 230 | 0 | 0 | -1 | 197.263 | 0.49517 | 121.9264 | 0.44464 | 123.2054 | 1.2518 | 8.136 | 16.2592 | 9.2468
593 | B59 | IEEE 118 Bus Test Case | Line 59-60 | 230 | 0 | 0 | -1 | 322.9909 | 0.81078 | 131.0733 | 0.75312 | 131.8579 | 2.0496 | 8.136 | 16.2592 | 9.2468
594 | B59 | IEEE 118 Bus Test Case | Load 59 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 8.136 | 16.2592 | 9.2468
595 | B59 | IEEE 118 Bus Test Case | Line 56-59 C1 | 230 | 0 | 0 | -1 | 173.4704 | 0.43545 | 127.9218 | 0.39132 | 129.1966 | 1.1008 | 8.136 | 16.2592 | 9.2468
596 | B59 | IEEE 118 Bus Test Case | Tx 63-59 | 230 | 0 | 0 | -1 | 1211.4733 | 3.0411 | 123.9819 | 2.8716 | 124.6479 | 7.6875 | 8.136 | 16.2592 | 9.2468
597 | B59 | IEEE 118 Bus Test Case | Line 56-59 C2 | 230 | 0 | 0 | -1 | 181.7827 | 0.45631 | 128.2983 | 0.41007 | 129.5732 | 1.1535 | 8.136 | 16.2592 | 9.2468
598 | B59 | IEEE 118 Bus Test Case | Line 59-61 | 230 | 0 | 0 | -1 | 329.2534 | 0.8265 | 131.7142 | 0.76648 | 132.515 | 2.0893 | 8.136 | 16.2592 | 9.2468
599 | B59 | IEEE 118 Bus Test Case | Tx 59-127 | 230 | 0 | 0 | -1 | 989.4933 | 2.4838 | 126.7854 | 1.962 | 129.9159 | 6.2789 | 8.136 | 16.2592 | 9.2468
600 | B63 | IEEE 118 Bus Test Case | Tx 59-127 | 500 | 0 | 0 | -1 | 3426.2979 | 3.9563 | -55.9334 | 3.6219 | -54.6707 | 10.2046 | 3.6494 | 7.0331 | 4.0572
601 | B63 | IEEE 118 Bus Test Case | Line 63-64 | 500 | 0 | 0 | -1 | 1880.9163 | 2.1719 | 125.7465 | 2.038 | 126.5101 | 5.602 | 3.6494 | 7.0331 | 4.0572
602 | B63 | IEEE 118 Bus Test Case | Tx 63-59 | 500 | 0 | 0 | -1 | 1547.1728 | 1.7865 | 122.0242 | 1.5849 | 123.8108 | 4.608 | 3.6494 | 7.0331 | 4.0572
603 | B54 | IEEE 118 Bus Test Case | Tx 63-59 | 230 | 0 | 0 | -1 | 2608.0878 | 6.5469 | -52.1642 | 5.7491 | -50.3929 | 15.1737 | 5.8146 | 9.8454 | 6.6195
604 | B54 | IEEE 118 Bus Test Case | Line 49-54 C1 | 230 | 0 | 0 | -1 | 266.0479 | 0.66784 | 131.8945 | 0.63258 | 132.5786 | 1.5479 | 5.8146 | 9.8454 | 6.6195
605 | B54 | IEEE 118 Bus Test Case | Line 49-54 C2 | 230 | 0 | 0 | -1 | 261.1237 | 0.65548 | 134.3454 | 0.62087 | 135.0295 | 1.5192 | 5.8146 | 9.8454 | 6.6195
606 | B54 | IEEE 118 Bus Test Case | Load 54 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8146 | 9.8454 | 6.6195
607 | B54 | IEEE 118 Bus Test Case | Line 53-54 | 230 | 0 | 0 | -1 | 106.5769 | 0.26753 | 129.9334 | 0.25345 | 130.6141 | 0.62006 | 5.8146 | 9.8454 | 6.6195
608 | B54 | IEEE 118 Bus Test Case | Line 54-56 | 230 | 0 | 0 | -1 | 903.7046 | 2.2685 | 132.7779 | 2.1531 | 133.4245 | 5.2577 | 5.8146 | 9.8454 | 6.6195
609 | B54 | IEEE 118 Bus Test Case | Line 54-59 | 230 | 0 | 0 | -1 | 275.9113 | 0.6926 | 127.3724 | 0.6582 | 128.0023 | 1.6052 | 5.8146 | 9.8454 | 6.6195
610 | B54 | IEEE 118 Bus Test Case | Line 54-55 | 230 | 0 | 0 | -1 | 144.4896 | 0.3627 | 128.3253 | 0.3444 | 128.9642 | 0.84063 | 5.8146 | 9.8454 | 6.6195
611 | B54 | IEEE 118 Bus Test Case | Tx 54-126 | 230 | 0 | 0 | -1 | 668.6301 | 1.6784 | 116.695 | 1.1165 | 118.4017 | 3.8901 | 5.8146 | 9.8454 | 6.6195
612 | B24 | IEEE 118 Bus Test Case | Tx 54-126 | 230 | 0 | 0 | -1 | 1186.1082 | 2.9774 | -45.6447 | 2.8798 | -45.7081 | 6.6394 | 2.8878 | 4.2485 | 3.0043
613 | B24 | IEEE 118 Bus Test Case | Gen 24 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8878 | 4.2485 | 3.0043
614 | B24 | IEEE 118 Bus Test Case | Line 24-70 | 230 | 0 | 0 | -1 | 173.7072 | 0.43604 | 119.1886 | 0.43218 | 119.206 | 0.97235 | 2.8878 | 4.2485 | 3.0043
615 | B24 | IEEE 118 Bus Test Case | Line 23-24 | 230 | 0 | 0 | -1 | 852.2431 | 2.1393 | 137.698 | 2.0491 | 137.7181 | 4.7705 | 2.8878 | 4.2485 | 3.0043
616 | B24 | IEEE 118 Bus Test Case | Line 24-72 | 230 | 0 | 0 | -1 | 167.7121 | 0.42099 | 132.9044 | 0.41726 | 132.9218 | 0.93879 | 2.8878 | 4.2485 | 3.0043
617 | B77 | IEEE 118 Bus Test Case | Line 24-72 | 230 | 0 | 0 | -1 | 3748.3589 | 9.4092 | -43.8161 | 8.7671 | -43.7014 | 20.609 | 8.8198 | 12.5266 | 9.4873
618 | B77 | IEEE 118 Bus Test Case | Gen 77 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8198 | 12.5266 | 9.4873
619 | B77 | IEEE 118 Bus Test Case | Line 69-77 | 230 | 0 | 0 | -1 | 755.3517 | 1.8961 | 134.7908 | 1.8036 | 134.6812 | 4.153 | 8.8198 | 12.5266 | 9.4873
620 | B77 | IEEE 118 Bus Test Case | Line 76-77 | 230 | 0 | 0 | -1 | 173.1964 | 0.43476 | 128.9065 | 0.41589 | 128.8347 | 0.95226 | 8.8198 | 12.5266 | 9.4873
621 | B77 | IEEE 118 Bus Test Case | Line 77-78 | 230 | 0 | 0 | -1 | 506.5111 | 1.2715 | 131.3134 | 1.166 | 131.4697 | 2.7849 | 8.8198 | 12.5266 | 9.4873
622 | B77 | IEEE 118 Bus Test Case | Line 75-77 | 230 | 0 | 0 | -1 | 227.6522 | 0.57146 | 131.7998 | 0.54666 | 131.728 | 1.2517 | 8.8198 | 12.5266 | 9.4873
623 | B77 | IEEE 118 Bus Test Case | Line 77-80 C1 | 230 | 0 | 0 | -1 | 1105.8212 | 2.7759 | 138.3562 | 2.5456 | 138.5125 | 6.08 | 8.8198 | 12.5266 | 9.4873
624 | B77 | IEEE 118 Bus Test Case | Line 77-80 C2 | 230 | 0 | 0 | -1 | 521.2072 | 1.3083 | 134.6821 | 1.1998 | 134.8384 | 2.8657 | 8.8198 | 12.5266 | 9.4873
625 | B77 | IEEE 118 Bus Test Case | Line 77-82 | 230 | 0 | 0 | -1 | 469.3323 | 1.1781 | 145.0643 | 1.1164 | 145.5191 | 2.5805 | 8.8198 | 12.5266 | 9.4873
626 | B77 | IEEE 118 Bus Test Case | Load 77 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8198 | 12.5266 | 9.4873
627 | B12 | IEEE 118 Bus Test Case | Load 77 | 230 | 0 | 0 | -1 | 2450.9397 | 6.1524 | -47.9589 | 5.4793 | -47.1666 | 15.2011 | 5.5346 | 9.5572 | 6.257
628 | B12 | IEEE 118 Bus Test Case | Line 11-12 | 230 | 0 | 0 | -1 | 612.0418 | 1.5364 | 131.2733 | 1.4717 | 131.2687 | 3.796 | 5.5346 | 9.5572 | 6.257
629 | B12 | IEEE 118 Bus Test Case | Line 7-12 | 230 | 0 | 0 | -1 | 278.6931 | 0.69958 | 128.0798 | 0.66877 | 128.0463 | 1.7285 | 5.5346 | 9.5572 | 6.257
630 | B12 | IEEE 118 Bus Test Case | Line 12-14 | 230 | 0 | 0 | -1 | 191.1872 | 0.47992 | 134.0761 | 0.46476 | 134.1995 | 1.1858 | 5.5346 | 9.5572 | 6.257
631 | B12 | IEEE 118 Bus Test Case | Line 2-12 | 230 | 0 | 0 | -1 | 64.4778 | 0.16185 | 129.4784 | 0.15472 | 129.4449 | 0.3999 | 5.5346 | 9.5572 | 6.257
632 | B12 | IEEE 118 Bus Test Case | Line 3-12 | 230 | 0 | 0 | -1 | 84.081 | 0.21106 | 128.9407 | 0.20177 | 128.9072 | 0.52148 | 5.5346 | 9.5572 | 6.257
633 | B12 | IEEE 118 Bus Test Case | Line 12-16 | 230 | 0 | 0 | -1 | 221.8246 | 0.55683 | 133.1331 | 0.538 | 133.2709 | 1.3758 | 5.5346 | 9.5572 | 6.257
634 | B12 | IEEE 118 Bus Test Case | Load 12 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5346 | 9.5572 | 6.257
635 | B12 | IEEE 118 Bus Test Case | Line 12-117 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5346 | 9.5572 | 6.257
636 | B12 | IEEE 118 Bus Test Case | Tx 12-120 | 230 | 0 | 0 | -1 | 999.9883 | 2.5102 | 133.4087 | 1.9861 | 135.8283 | 6.2021 | 5.5346 | 9.5572 | 6.257
637 | B61 | IEEE 118 Bus Test Case | Tx 12-120 | 230 | 0 | 0 | -1 | 3627.9857 | 9.107 | -55.0449 | 8.1479 | -53.9995 | 23.5048 | 8.2266 | 17.6029 | 9.3408
638 | B61 | IEEE 118 Bus Test Case | Line 59-61 | 230 | 0 | 0 | -1 | 320.655 | 0.80491 | 128.0883 | 0.73897 | 129.1671 | 2.0774 | 8.2266 | 17.6029 | 9.3408
639 | B61 | IEEE 118 Bus Test Case | Line 61-62 | 230 | 0 | 0 | -1 | 430.8229 | 1.0815 | 131.9818 | 1.0239 | 132.5096 | 2.7912 | 8.2266 | 17.6029 | 9.3408
640 | B61 | IEEE 118 Bus Test Case | Line 60-61 | 230 | 0 | 0 | -1 | 464.7492 | 1.1666 | 129.1213 | 1.0868 | 129.9695 | 3.011 | 8.2266 | 17.6029 | 9.3408
641 | B61 | IEEE 118 Bus Test Case | Tx 64-61 | 230 | 0 | 0 | -1 | 1504.3954 | 3.7764 | 121.7024 | 3.5559 | 122.4364 | 9.7466 | 8.2266 | 17.6029 | 9.3408
642 | B61 | IEEE 118 Bus Test Case | Tx 61-128 | 230 | 0 | 0 | -1 | 914.9197 | 2.2966 | 123.7881 | 1.7596 | 125.6398 | 5.9275 | 8.2266 | 17.6029 | 9.3408
643 | B46 | IEEE 118 Bus Test Case | Tx 61-128 | 230 | 0 | 0 | -1 | 1673.7143 | 4.2014 | -50.793 | 3.6821 | -49.5341 | 9.6333 | 3.7247 | 6.7707 | 4.2453
644 | B46 | IEEE 118 Bus Test Case | Line 46-47 | 230 | 0 | 0 | -1 | 462.6603 | 1.1614 | 133.02 | 1.1219 | 133.2398 | 2.6629 | 3.7247 | 6.7707 | 4.2453
645 | B46 | IEEE 118 Bus Test Case | Line 46-48 | 230 | 0 | 0 | -1 | 326.2634 | 0.81899 | 134.0366 | 0.78708 | 134.2899 | 1.8779 | 3.7247 | 6.7707 | 4.2453
646 | B46 | IEEE 118 Bus Test Case | Shunt 46 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7247 | 6.7707 | 4.2453
647 | B46 | IEEE 118 Bus Test Case | Line 45-46 | 230 | 0 | 0 | -1 | 284.1405 | 0.71325 | 131.5254 | 0.69044 | 131.7063 | 1.6354 | 3.7247 | 6.7707 | 4.2453
648 | B46 | IEEE 118 Bus Test Case | Load 46 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7247 | 6.7707 | 4.2453
649 | B46 | IEEE 118 Bus Test Case | Tx 46-124 | 230 | 0 | 0 | -1 | 607.0831 | 1.5239 | 122.6115 | 1.0926 | 124.0692 | 3.4941 | 3.7247 | 6.7707 | 4.2453
650 | B50 | IEEE 118 Bus Test Case | Tx 46-124 | 230 | 0 | 0 | -1 | 1310.4847 | 3.2896 | -46.2121 | 3.1387 | -45.9455 | 6.6361 | 3.1511 | 4.4587 | 3.3088
651 | B50 | IEEE 118 Bus Test Case | Line 49-50 | 230 | 0 | 0 | -1 | 1007.9747 | 2.5302 | 135.4724 | 2.4133 | 135.7526 | 5.1042 | 3.1511 | 4.4587 | 3.3088
652 | B50 | IEEE 118 Bus Test Case | Line 50-57 | 230 | 0 | 0 | -1 | 304.3912 | 0.76409 | 128.2018 | 0.72995 | 128.4323 | 1.5414 | 3.1511 | 4.4587 | 3.3088
653 | B50 | IEEE 118 Bus Test Case | Load 50 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1511 | 4.4587 | 3.3088
654 | B118 | IEEE 118 Bus Test Case | Load 50 | 230 | 0 | 0 | -1 | 1225.4753 | 3.0762 | -44.2318 | 3.0193 | -44.1612 | 6.3267 | 3.024 | 4.2782 | 3.0956
655 | B118 | IEEE 118 Bus Test Case | Line 76-118 | 230 | 0 | 0 | -1 | 378.5188 | 0.95016 | 136.3576 | 0.93221 | 136.4723 | 1.9541 | 3.024 | 4.2782 | 3.0956
656 | B118 | IEEE 118 Bus Test Case | Line 75-118 | 230 | 0 | 0 | -1 | 846.9855 | 2.1261 | 135.5048 | 2.0872 | 135.5558 | 4.3727 | 3.024 | 4.2782 | 3.0956
657 | B118 | IEEE 118 Bus Test Case | Load 118 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.024 | 4.2782 | 3.0956
658 | B44 | IEEE 118 Bus Test Case | Load 118 | 230 | 0 | 0 | -1 | 686.8255 | 1.7241 | -48.414 | 1.6858 | -48.194 | 3.6186 | 1.6889 | 2.3909 | 1.7359
659 | B44 | IEEE 118 Bus Test Case | Line 43-44 | 230 | 0 | 0 | -1 | 200.9888 | 0.50453 | 131.2545 | 0.50019 | 131.3397 | 1.0589 | 1.6889 | 2.3909 | 1.7359
660 | B44 | IEEE 118 Bus Test Case | Load 44 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6889 | 2.3909 | 1.7359
661 | B44 | IEEE 118 Bus Test Case | Line 44-45 | 230 | 0 | 0 | -1 | 485.8415 | 1.2196 | 131.7231 | 1.1856 | 132.0027 | 2.5597 | 1.6889 | 2.3909 | 1.7359
662 | B44 | IEEE 118 Bus Test Case | Shunt 44 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6889 | 2.3909 | 1.7359
663 | B114 | IEEE 118 Bus Test Case | Shunt 44 | 230 | 0 | 0 | -1 | 1072.3064 | 2.6917 | -42.708 | 2.567 | -42.5033 | 5.9763 | 2.5772 | 3.6631 | 2.7156
664 | B114 | IEEE 118 Bus Test Case | Line 32-114 | 230 | 0 | 0 | -1 | 636.4012 | 1.5975 | 136.6928 | 1.525 | 136.8924 | 3.5468 | 2.5772 | 3.6631 | 2.7156
665 | B114 | IEEE 118 Bus Test Case | Line 114-115 | 230 | 0 | 0 | -1 | 435.9908 | 1.0944 | 138.1665 | 1.0422 | 138.381 | 2.4299 | 2.5772 | 3.6631 | 2.7156
666 | B114 | IEEE 118 Bus Test Case | Load 114 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5772 | 3.6631 | 2.7156
667 | B57 | IEEE 118 Bus Test Case | Load 114 | 230 | 0 | 0 | -1 | 1041.4129 | 2.6142 | -48.2106 | 2.5114 | -47.7971 | 5.2662 | 2.5198 | 3.565 | 2.6294
668 | B57 | IEEE 118 Bus Test Case | Line 56-57 | 230 | 0 | 0 | -1 | 640.2154 | 1.6071 | 129.1188 | 1.5357 | 129.5631 | 3.2374 | 2.5198 | 3.565 | 2.6294
669 | B57 | IEEE 118 Bus Test Case | Line 50-57 | 230 | 0 | 0 | -1 | 402.9985 | 1.0116 | 136.0344 | 0.9798 | 136.3425 | 2.0379 | 2.5198 | 3.565 | 2.6294
670 | B57 | IEEE 118 Bus Test Case | Load 57 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5198 | 3.565 | 2.6294
671 | B58 | IEEE 118 Bus Test Case | Load 57 | 230 | 0 | 0 | -1 | 1075.9597 | 2.7009 | -48.7601 | 2.5884 | -48.2545 | 5.4822 | 2.5977 | 3.6763 | 2.7171
672 | B58 | IEEE 118 Bus Test Case | Line 51-58 | 230 | 0 | 0 | -1 | 456.3656 | 1.1456 | 133.403 | 1.1052 | 133.8395 | 2.3253 | 2.5977 | 3.6763 | 2.7171
673 | B58 | IEEE 118 Bus Test Case | Load 58 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5977 | 3.6763 | 2.7171
674 | B58 | IEEE 118 Bus Test Case | Line 56-58 | 230 | 0 | 0 | -1 | 620.1585 | 1.5567 | 129.6483 | 1.4845 | 130.1866 | 3.1598 | 2.5977 | 3.6763 | 2.7171
675 | B55 | IEEE 118 Bus Test Case | Line 56-58 | 230 | 0 | 0 | -1 | 2069.2139 | 5.1942 | -51.4583 | 4.7379 | -50.1704 | 11.5975 | 4.7754 | 7.021 | 5.2415
676 | B55 | IEEE 118 Bus Test Case | Gen 55 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7754 | 7.021 | 5.2415
677 | B55 | IEEE 118 Bus Test Case | Line 54-55 | 230 | 0 | 0 | -1 | 389.7578 | 0.97838 | 124.7858 | 0.87385 | 126.3084 | 2.1845 | 4.7754 | 7.021 | 5.2415
678 | B55 | IEEE 118 Bus Test Case | Line 55-56 | 230 | 0 | 0 | -1 | 1368.7418 | 3.4358 | 129.9019 | 3.122 | 131.2753 | 7.6715 | 4.7754 | 7.021 | 5.2415
679 | B55 | IEEE 118 Bus Test Case | Load 55 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7754 | 7.021 | 5.2415
680 | B55 | IEEE 118 Bus Test Case | Line 55-59 | 230 | 0 | 0 | -1 | 312.0147 | 0.78323 | 127.2635 | 0.74511 | 127.8996 | 1.7488 | 4.7754 | 7.021 | 5.2415
681 | B40 | IEEE 118 Bus Test Case | Line 55-59 | 230 | 0 | 0 | -1 | 1062.8476 | 2.668 | -47.0225 | 2.6219 | -46.8579 | 5.6775 | 2.6257 | 3.7178 | 2.6874
682 | B40 | IEEE 118 Bus Test Case | Line 40-41 | 230 | 0 | 0 | -1 | 175.6873 | 0.44101 | 129.259 | 0.43161 | 129.4631 | 0.93849 | 2.6257 | 3.7178 | 2.6874
683 | B40 | IEEE 118 Bus Test Case | Line 37-40 | 230 | 0 | 0 | -1 | 352.405 | 0.88461 | 136.2004 | 0.87109 | 136.3355 | 1.8825 | 2.6257 | 3.7178 | 2.6874
684 | B40 | IEEE 118 Bus Test Case | Line 39-40 | 230 | 0 | 0 | -1 | 358.2687 | 0.89933 | 133.0585 | 0.88559 | 133.1936 | 1.9138 | 2.6257 | 3.7178 | 2.6874
685 | B40 | IEEE 118 Bus Test Case | Line 40-42 | 230 | 0 | 0 | -1 | 177.6387 | 0.44591 | 130.0972 | 0.43641 | 130.3014 | 0.94891 | 2.6257 | 3.7178 | 2.6874
686 | B40 | IEEE 118 Bus Test Case | Load 40 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6257 | 3.7178 | 2.6874
687 | B35 | IEEE 118 Bus Test Case | Load 40 | 230 | 0 | 0 | -1 | 1436.2141 | 3.6052 | -50.0663 | 3.5237 | -49.8719 | 8.2408 | 3.5304 | 5.0844 | 3.6423
688 | B35 | IEEE 118 Bus Test Case | Line 35-36 | 230 | 0 | 0 | -1 | 757.5665 | 1.9017 | 131.9741 | 1.8585 | 132.1695 | 4.3468 | 3.5304 | 5.0844 | 3.6423
689 | B35 | IEEE 118 Bus Test Case | Line 35-37 | 230 | 0 | 0 | -1 | 679.6633 | 1.7061 | 127.6594 | 1.6677 | 127.8531 | 3.8998 | 3.5304 | 5.0844 | 3.6423
690 | B35 | IEEE 118 Bus Test Case | Load 35 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5304 | 5.0844 | 3.6423
691 | B53 | IEEE 118 Bus Test Case | Load 35 | 230 | 0 | 0 | -1 | 824.1724 | 2.0689 | -53.6137 | 1.9959 | -52.9714 | 4.4937 | 2.0019 | 2.8478 | 2.0854
692 | B53 | IEEE 118 Bus Test Case | Line 53-54 | 230 | 0 | 0 | -1 | 559.6027 | 1.4047 | 124.4703 | 1.3501 | 125.1581 | 3.0512 | 2.0019 | 2.8478 | 2.0854
693 | B53 | IEEE 118 Bus Test Case | Line 52-53 | 230 | 0 | 0 | -1 | 265.5425 | 0.66657 | 130.4266 | 0.64801 | 130.9282 | 1.4478 | 2.0019 | 2.8478 | 2.0854
694 | B53 | IEEE 118 Bus Test Case | Load 53 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0019 | 2.8478 | 2.0854
695 | B101 | IEEE 118 Bus Test Case | Load 53 | 230 | 0 | 0 | -1 | 1072.3334 | 2.6918 | -37.8928 | 2.575 | -37.7691 | 5.9852 | 2.5846 | 3.6745 | 2.7158
696 | B101 | IEEE 118 Bus Test Case | Line 101-102 | 230 | 0 | 0 | -1 | 437.581 | 1.0984 | 143.3601 | 1.0639 | 143.4117 | 2.4423 | 2.5846 | 3.6745 | 2.7158
697 | B101 | IEEE 118 Bus Test Case | Line 100-101 | 230 | 0 | 0 | -1 | 634.9291 | 1.5938 | 141.2437 | 1.5115 | 141.3997 | 3.5438 | 2.5846 | 3.6745 | 2.7158
698 | B101 | IEEE 118 Bus Test Case | Load 101 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5846 | 3.6745 | 2.7158
699 | B48 | IEEE 118 Bus Test Case | Load 101 | 230 | 0 | 0 | -1 | 1684.4403 | 4.2283 | -46.3037 | 3.9575 | -46.0192 | 8.7567 | 3.9797 | 5.64 | 4.2558
700 | B48 | IEEE 118 Bus Test Case | Shunt 48 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9797 | 5.64 | 4.2558
701 | B48 | IEEE 118 Bus Test Case | Line 48-49 | 230 | 0 | 0 | -1 | 1360.2959 | 3.4146 | 134.3294 | 3.2104 | 134.6068 | 7.0716 | 3.9797 | 5.64 | 4.2558
702 | B48 | IEEE 118 Bus Test Case | Load 48 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9797 | 5.64 | 4.2558
703 | B48 | IEEE 118 Bus Test Case | Line 46-48 | 230 | 0 | 0 | -1 | 324.5757 | 0.81476 | 131.0419 | 0.7481 | 131.2934 | 1.6873 | 3.9797 | 5.64 | 4.2558

## AporteGeneradores
0 | Terminal | Grid | Connected Element (Branch) | Nominal Voltage (kV) | Fault Voltage (kV) | Fault Voltage Angle (deg) | c-Factor | Sk" (MVA) | Ik" (kA) | Ik" Angle (deg) | Ik (kA) | Ik Angle (deg) | ip (kA) | Ib (kA) | ib (kA) | Ith (kA)
391 | B1 | IEEE 118 Bus Test Case | Gen 1 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3912 | 3.3922 | 2.5043
443 | B119 | IEEE 118 Bus Test Case | Gen 10 | 22 | 0 | 0 | -1 | 2809.8629 | 73.7398 | -55.9246 | 56.1932 | -56.0875 | 198.0073 | 78.4487 | 168.3613 | 99.6674
494 | B135 | IEEE 118 Bus Test Case | Gen 100 | 20 | 0 | 0 | -1 | 1798.7592 | 51.9257 | -42.316 | 34.3058 | -38.1991 | 129.1549 | 96.7198 | 227.4024 | 111.333
486 | B136 | IEEE 118 Bus Test Case | Gen 103 | 13.8 | 0 | 0 | -1 | 765.1842 | 32.013 | -46.0884 | 22.0907 | -45.2195 | 75.5621 | 84.2932 | 147.6219 | 101.0443
487 | B137 | IEEE 118 Bus Test Case | Gen 103 | 13.8 | 0 | 0 | -1 | 1120.1858 | 46.8652 | -39.5877 | 36.5845 | -38.6112 | 116.3123 | 37.4284 | 77.0017 | 43.6897
191 | B104 | IEEE 118 Bus Test Case | Gen 104 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0834 | 4.3874 | 3.3701
396 | B105 | IEEE 118 Bus Test Case | Gen 105 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2193 | 4.5756 | 3.5385
385 | B107 | IEEE 118 Bus Test Case | Gen 107 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4112 | 1.9971 | 1.4724
148 | B110 | IEEE 118 Bus Test Case | Gen 110 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5164 | 3.6125 | 2.8891
489 | B137 | IEEE 118 Bus Test Case | Gen 111 | 13.8 | 0 | 0 | -1 | 675.6723 | 28.2681 | -41.4597 | 18.6434 | -40.3187 | 70.1571 | 37.4284 | 77.0017 | 43.6897
490 | B121 | IEEE 118 Bus Test Case | Gen 111 | 20 | 0 | 0 | -1 | 4205.8053 | 121.4111 | -49.8684 | 96.4886 | -49.0516 | 327.9259 | 98.5344 | 268.3536 | 118.2068
110 | B112 | IEEE 118 Bus Test Case | Gen 112 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4788 | 2.0928 | 1.6023
254 | B116 | IEEE 118 Bus Test Case | Gen 116 | 500 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2073 | 11.1173 | 6.9722
480 | B120 | IEEE 118 Bus Test Case | Gen 12 | 15.5 | 0 | 0 | -1 | 999.9883 | 37.248 | -46.5913 | 29.4705 | -44.1717 | 92.0308 | 82.1258 | 141.8162 | 92.846
481 | B126 | IEEE 118 Bus Test Case | Gen 12 | 13.8 | 0 | 0 | -1 | 2608.0878 | 109.1145 | -52.1642 | 95.819 | -50.3929 | 252.8952 | 96.9104 | 164.0907 | 110.3254
164 | B15 | IEEE 118 Bus Test Case | Gen 15 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8791 | 6.9433 | 5.1472
277 | B18 | IEEE 118 Bus Test Case | Gen 18 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8503 | 5.4879 | 4.0233
257 | B19 | IEEE 118 Bus Test Case | Gen 19 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1331 | 5.8726 | 4.3203
613 | B24 | IEEE 118 Bus Test Case | Gen 24 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8878 | 4.2485 | 3.0043
491 | B121 | IEEE 118 Bus Test Case | Gen 25 | 20 | 0 | 0 | -1 | 1752.7731 | 50.5982 | -51.3101 | 32.1499 | -50.4163 | 136.6634 | 98.5344 | 268.3536 | 118.2068
497 | B122 | IEEE 118 Bus Test Case | Gen 26 | 24 | 0 | 0 | -1 | 1888.2439 | 45.4241 | -45.9902 | 38.1976 | -44.9305 | 123.1341 | 88.8274 | 231.1296 | 112.0047
270 | B27 | IEEE 118 Bus Test Case | Gen 27 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3093 | 4.7177 | 3.5391
450 | B123 | IEEE 118 Bus Test Case | Gen 31 | 13.8 | 0 | 0 | -1 | 567.9566 | 23.7616 | -37.3937 | 17.1527 | -31.4164 | 55.75 | 60.8204 | 108.7673 | 69.1226
451 | B124 | IEEE 118 Bus Test Case | Gen 31 | 13.8 | 0 | 0 | -1 | 1673.7143 | 70.0231 | -50.793 | 61.3679 | -49.5341 | 160.5548 | 62.0783 | 112.8445 | 70.755
128 | B32 | IEEE 118 Bus Test Case | Gen 32 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8416 | 5.4761 | 4.1354
405 | B34 | IEEE 118 Bus Test Case | Gen 34 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6767 | 6.8978 | 4.8667
542 | B36 | IEEE 118 Bus Test Case | Gen 36 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6222 | 5.2094 | 3.7381
330 | B4 | IEEE 118 Bus Test Case | Gen 4 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9887 | 7.6756 | 5.4364
452 | B124 | IEEE 118 Bus Test Case | Gen 46 | 13.8 | 0 | 0 | -1 | 607.0831 | 25.3985 | -57.3885 | 18.2107 | -55.9308 | 58.2358 | 62.0783 | 112.8445 | 70.755
459 | B125 | IEEE 118 Bus Test Case | Gen 49 | 20 | 0 | 0 | -1 | 1805.1008 | 52.1088 | -54.9399 | 34.3409 | -50.8742 | 127.0453 | 127.1943 | 269.9191 | 152.9651
460 | B127 | IEEE 118 Bus Test Case | Gen 49 | 20 | 0 | 0 | -1 | 3608.8864 | 104.1796 | -53.721 | 92.6148 | -52.3259 | 263.3561 | 93.5641 | 186.9808 | 106.3377
482 | B126 | IEEE 118 Bus Test Case | Gen 54 | 13.8 | 0 | 0 | -1 | 668.6301 | 27.9735 | -63.305 | 18.6084 | -61.5983 | 64.8342 | 96.9104 | 164.0907 | 110.3254
676 | B55 | IEEE 118 Bus Test Case | Gen 55 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7754 | 7.021 | 5.2415
562 | B56 | IEEE 118 Bus Test Case | Gen 56 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6934 | 8.7619 | 6.3766
461 | B127 | IEEE 118 Bus Test Case | Gen 59 | 20 | 0 | 0 | -1 | 989.4934 | 28.5642 | -53.2146 | 22.5635 | -50.0841 | 72.2076 | 93.5641 | 186.9808 | 106.3377
249 | B6 | IEEE 118 Bus Test Case | Gen 6 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7898 | 5.5053 | 4.0727
465 | B128 | IEEE 118 Bus Test Case | Gen 61 | 20 | 0 | 0 | -1 | 914.9197 | 26.4115 | -56.2119 | 20.235 | -54.3602 | 68.1667 | 94.6064 | 202.4334 | 107.4187
466 | B129 | IEEE 118 Bus Test Case | Gen 61 | 24 | 0 | 0 | -1 | 10018.8168 | 241.0153 | -54.7647 | 201.3513 | -53.7078 | 642.7734 | 204.6071 | 425.0231 | 250.7571
318 | B62 | IEEE 118 Bus Test Case | Gen 62 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9154 | 8.675 | 6.3726
468 | B129 | IEEE 118 Bus Test Case | Gen 65 | 24 | 0 | 0 | -1 | 2815.929 | 67.7407 | -50.9209 | 51.8933 | -49.0185 | 180.6605 | 204.6071 | 425.0231 | 250.7571
469 | B130 | IEEE 118 Bus Test Case | Gen 65 | 24 | 0 | 0 | -1 | 8418.56 | 202.5191 | -54.9156 | 168.8151 | -53.9401 | 538.7419 | 171.5817 | 371.2362 | 210.3628
471 | B130 | IEEE 118 Bus Test Case | Gen 66 | 24 | 0 | 0 | -1 | 2708.1877 | 65.1489 | -54.2858 | 48.2645 | -53.1814 | 173.3092 | 171.5817 | 371.2362 | 210.3628
472 | B134 | IEEE 118 Bus Test Case | Gen 66 | 20 | 0 | 0 | -1 | 3693.2551 | 106.6151 | -40.9227 | 92.1409 | -40.3139 | 277.1656 | 93.329 | 235.2546 | 109.5948
446 | B131 | IEEE 118 Bus Test Case | Gen 69 | 22 | 0 | 0 | -1 | 2776.494 | 72.8641 | -58.1011 | 55.4839 | -58.1851 | 189.2473 | 166.5985 | 338.0835 | 195.8848
373 | B70 | IEEE 118 Bus Test Case | Gen 70 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8486 | 5.5299 | 3.965
210 | B72 | IEEE 118 Bus Test Case | Gen 72 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5957 | 2.2582 | 1.6241
440 | B73 | IEEE 118 Bus Test Case | Gen 73 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 1.79 | 2.5395 | 1.8223
21 | B74 | IEEE 118 Bus Test Case | Gen 74 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1026 | 4.3915 | 3.1775
114 | B76 | IEEE 118 Bus Test Case | Gen 76 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6568 | 3.7584 | 2.7145
618 | B77 | IEEE 118 Bus Test Case | Gen 77 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8198 | 12.5266 | 9.4873
347 | B8 | IEEE 118 Bus Test Case | Gen 8 | 500 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9558 | 4.6866 | 3.2708
476 | B132 | IEEE 118 Bus Test Case | Gen 80 | 22 | 0 | 0 | -1 | 3077.4988 | 80.7634 | -51.2174 | 63.4468 | -50.0257 | 205.9845 | 139.3737 | 283.1941 | 163.1602
13 | B85 | IEEE 118 Bus Test Case | Gen 85 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.673 | 5.2828 | 3.8788
456 | B133 | IEEE 118 Bus Test Case | Gen 87 | 13.8 | 0 | 0 | -1 | 593.8365 | 24.8443 | -41.5791 | 17.5695 | -40.8019 | 64.0247 | 28.0166 | 58.6794 | 32.7806
457 | B125 | IEEE 118 Bus Test Case | Gen 87 | 20 | 0 | 0 | -1 | 5218.6944 | 150.6507 | -52.0637 | 125.0967 | -50.2988 | 367.2983 | 127.1943 | 269.9191 | 152.9651
474 | B134 | IEEE 118 Bus Test Case | Gen 89 | 20 | 0 | 0 | -1 | 2531.7105 | 73.0842 | -40.399 | 60.3487 | -39.2613 | 189.9958 | 93.329 | 235.2546 | 109.5948
475 | B132 | IEEE 118 Bus Test Case | Gen 89 | 22 | 0 | 0 | -1 | 6079.8779 | 159.5554 | -49.5318 | 137.5689 | -48.6827 | 406.9411 | 139.3737 | 283.1941 | 163.1602
218 | B90 | IEEE 118 Bus Test Case | Gen 90 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1567 | 4.4947 | 3.3336
224 | B91 | IEEE 118 Bus Test Case | Gen 91 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4777 | 3.5089 | 2.579
430 | B92 | IEEE 118 Bus Test Case | Gen 92 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 6.011 | 8.732 | 6.5556
214 | B99 | IEEE 118 Bus Test Case | Gen 99 | 230 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 3.237 | 4.6119 | 3.4327

## AportesCriticos
Terminal | Connected Element (Branch) | Fault Voltage (kV) | Sk" (MVA) | Ik" (kA) | Ik (kA)
B121 | Gen 111 | 0 | 4205.8053 | 121.4111 | 96.4886
B126 | Gen 12 | 0 | 2608.0878 | 109.1145 | 95.819
B129 | Gen 61 | 0 | 10018.8168 | 241.0153 | 201.3513
B130 | Gen 65 | 0 | 8418.56 | 202.5191 | 168.8151
B125 | Gen 87 | 0 | 5218.6944 | 150.6507 | 125.0967
B132 | Gen 89 | 0 | 6079.8779 | 159.5554 | 137.5689